## LDC
10/16/2017 Carleton College 03:04 PM
Panel Point Definition Report
Selection: ACDIN*
Point System Name: ACDIN.1ST RSTRMS.ZON:MODE
Point Name: ACDIN.1ST RSTRMS.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.AH1.CCV
Point Name: ACDIN.AH1.CCV
Point Type: LAO
Descriptor: AH1 CLG VLV
Value: 7.35
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.DSP
Point Name: ACDIN.AH1.DSP
Point Type: LAI
Descriptor: AH1 SA PRESS
Value: 1.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24996
COV Limit: 0.04
Point System Name: ACDIN.AH1.DSSP
Point Name: ACDIN.AH1.DSSP
Point Type: LAO
Descriptor: DUCT STATIC STPT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.ECN
Point Name: ACDIN.AH1.ECN
Point Type: LDO
Descriptor: ECONOMIZE MODE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.AH1.ERR
Point Name: ACDIN.AH1.ERR
Point Type: LAO
Descriptor: SPLY TEMP ERROR
Value: -1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.FBD
Point Name: ACDIN.AH1.FBD
Point Type: LAO
Descriptor: AHI FB DPRS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.FRZ
Point Name: ACDIN.AH1.FRZ
Point Type: LDI
Descriptor: AH1 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 03
Normally Closed: No
Point System Name: ACDIN.AH1.HCV
Point Name: ACDIN.AH1.HCV
Point Type: LAO
Descriptor: AH1 HTG VLV
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.HFBS
Point Name: ACDIN.AH1.HFBS
Point Type: LDO
Descriptor: HTG F/B SWITCH
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.AH1.HSP
Point Name: ACDIN.AH1.HSP
Point Type: LDI
Descriptor: AH1 HI STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 05
Normally Closed: Yes
Point System Name: ACDIN.AH1.LP1
Point Name: ACDIN.AH1.LP1
Point Type: LAO
Descriptor: MIX AIR LOOPOUT
Value: 14.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.LP2
Point Name: ACDIN.AH1.LP2
Point Type: LAO
Descriptor: RET FAN RESET
Value: 6.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.LPO
Point Name: ACDIN.AH1.LPO
Point Type: LAO
Descriptor: SUP TEMP LOOPOUT
Value: 81.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.MAD
Point Name: ACDIN.AH1.MAD
Point Type: LAO
Descriptor: AH1 MA DPRS
Value: 14.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.MAM
Point Name: ACDIN.AH1.MAM
Point Type: LAO
Descriptor: MIN DPR POS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.MAS
Point Name: ACDIN.AH1.MAS
Point Type: LAO
Descriptor: MIX AIR SETPNT
Value: 52.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.MAT
Point Name: ACDIN.AH1.MAT
Point Type: LAI
Descriptor: AH1 MA TEMP
Value: 64.47
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.MAX.DMPR.COMD
Point Name: ACDIN.AH1.MAX.DMPR.COMD
Point Type: LAO
Descriptor: MAX VAV DMPR
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: %
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.MOAD
Point Name: ACDIN.AH1.MOAD
Point Type: LAO
Descriptor: AH1 MIN OAD
Value: 14.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.MOD
Point Name: ACDIN.AH1.MOD
Point Type: LAO
Descriptor: AH1 MODE
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.NMBR.REQ.CLG
Point Name: ACDIN.AH1.NMBR.REQ.CLG
Point Type: LAO
Descriptor: NMBR REQ CLG
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UNITS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.OACFM
Point Name: ACDIN.AH1.OACFM
Point Type: LAI
Descriptor: AH1 OA CFM
Value: 0.136
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 3
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: 0.01509
COV Limit: 0.005
Point System Name: ACDIN.AH1.OAT
Point Name: ACDIN.AH1.OAT
Point Type: LAO
Descriptor: VIR OAT
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.OCC
Point Name: ACDIN.AH1.OCC
Point Type: LDO
Descriptor: OCC MODE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.AH1.RADPT
Point Name: ACDIN.AH1.RADPT
Point Type: LAO
Descriptor: RTRN DEW POINT
Value: -9.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.RAH
Point Name: ACDIN.AH1.RAH
Point Type: LAI
Descriptor: AH1 RA HUMID
Value: 3.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 1.0
Point System Name: ACDIN.AH1.RAT
Point Name: ACDIN.AH1.RAT
Point Type: LAI
Descriptor: AH1 RA TEMP
Value: 71.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 15 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.RDPS
Point Name: ACDIN.AH1.RDPS
Point Type: LAO
Descriptor: CL DN SPLY SETPT
Value: 53.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.RFN
Point Name: ACDIN.AH1.RFN
Point Type: L2SL
Descriptor: AH1 RFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 07 02
Inverted: No
Proof Point Address: 0 10 02
Normally Closed: No
Proof Delay: 10 Informational Text
Point System Name: ACDIN.AH1.RFNVFD
Point Name: ACDIN.AH1.RFNVFD
Point Type: LAO
Descriptor: AH1 RFN VFD
Value: 6.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 21 02
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.SAS
Point Name: ACDIN.AH1.SAS
Point Type: LAO
Descriptor: SUPPLY AIR SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.SAT
Point Name: ACDIN.AH1.SAT
Point Type: LAI
Descriptor: AH1 SA TEMP
Value: 59.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 15 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.SFN
Point Name: ACDIN.AH1.SFN
Point Type: L2SL
Descriptor: AH1 SFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 07 01
Inverted: No
Proof Point Address: 0 10 01
Normally Closed: No
Proof Delay: 10 Informational Text
Point System Name: ACDIN.AH1.SFNVFD
Point Name: ACDIN.AH1.SFNVFD
Point Type: LAO
Descriptor: AH1 SFN VFD
Value: 6.83
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 21 01
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.SMK
Point Name: ACDIN.AH1.SMK
Point Type: LDI
Descriptor: AH1 SMK ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 04
Normally Closed: No
Point System Name: ACDIN.AH1.SP1
Point Name: ACDIN.AH1.SP1
Point Type: LAO
Descriptor: SPLY STATIC RAMP
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.SSP
Point Name: ACDIN.AH1.SSP
Point Type: LAI
Descriptor: AH1 RM PRESS
Value: -0.083
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 3
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: -0.152
COV Limit: 0.001
Point System Name: ACDIN.AH1.T01
Point Name: ACDIN.AH1.T01
Point Type: LAO
Descriptor: SPLY SETPT TIMER
Value: 47110.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: SECS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.T04
Point Name: ACDIN.AH1.T04
Point Type: LAO
Descriptor: SPLY SPD TIMER
Value: 47110.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: SECS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.T05
Point Name: ACDIN.AH1.T05
Point Type: LAO
Descriptor: RTRN SPD TIMER
Value: 47105.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: SECS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH1.WCF
Point Name: ACDIN.AH1.WCF
Point Type: LDO
Descriptor: WUP WCD SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.AH3.MCL
Point Name: ACDIN.AH3.MCL
Point Type: LAO
Descriptor: MAX VAV CLG LOOP
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.CCV
Point Name: ACDIN.AH4.CCV
Point Type: LAO
Descriptor: AH4 CLG VLV
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 02 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.CLO
Point Name: ACDIN.AH4.CLO
Point Type: LAO
Descriptor: CLG LOOPOUT
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.DSP
Point Name: ACDIN.AH4.DSP
Point Type: LAI
Descriptor: AH4 SA PRESS
Value: 0.932
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 3
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24996
COV Limit: 0.1
Point System Name: ACDIN.AH4.DSSP
Point Name: ACDIN.AH4.DSSP
Point Type: LAO
Descriptor: DUCT STATC SETPT
Value: 1.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
Point System Name: ACDIN.AH4.EPSFN
Point Name: ACDIN.AH4.EPSFN
Point Type: L2SL
Descriptor: AH4 SFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 07 03
Inverted: No
Proof Point Address: 0 11 01
Normally Closed: No
Proof Delay: 60 Informational Text
Point System Name: ACDIN.AH4.FBD
Point Name: ACDIN.AH4.FBD
Point Type: LAO
Descriptor: AH1 FB DPRS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.FRZ
Point Name: ACDIN.AH4.FRZ
Point Type: LDI
Descriptor: AH4 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 02
Normally Closed: No
Point System Name: ACDIN.AH4.HCV
Point Name: ACDIN.AH4.HCV
Point Type: LAO
Descriptor: AH4 HTG VLV
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.HLO
Point Name: ACDIN.AH4.HLO
Point Type: LAO
Descriptor: HUM LOOPOUT
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.HMS
Point Name: ACDIN.AH4.HMS
Point Type: LAO
Descriptor: RM HUM STPT
Value: 50.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.HSP
Point Name: ACDIN.AH4.HSP
Point Type: LDI
Descriptor: AH4 HI STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 04
Normally Closed: Yes
Point System Name: ACDIN.AH4.HTG
Point Name: ACDIN.AH4.HTG
Point Type: LDO
Descriptor: VIRT.HTG MODE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.AH4.HUM
Point Name: ACDIN.AH4.HUM
Point Type: LAI
Descriptor: RM HUM
Value: 20.91
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.LPO
Point Name: ACDIN.AH4.LPO
Point Type: LAO
Descriptor: SPLY.LOOPOUT
Value: 5.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.OAT
Point Name: ACDIN.AH4.OAT
Point Type: LAO
Descriptor: VIRT.OUTSIDE.TEM
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.OCC
Point Name: ACDIN.AH4.OCC
Point Type: LDO
Descriptor: VIRT.ON/OFF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.AH4.RHV
Point Name: ACDIN.AH4.RHV
Point Type: LAO
Descriptor: AH4 RHT VLV
Value: 11.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 01 08
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.SAD1
Point Name: ACDIN.AH4.SAD1
Point Type: LDO
Descriptor: AH4 SA DPR1
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 08 02
Inverted: No
Point System Name: ACDIN.AH4.SAD2
Point Name: ACDIN.AH4.SAD2
Point Type: LDO
Descriptor: AH4 SA DPR2
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 08 03
Inverted: No
Point System Name: ACDIN.AH4.SAD3
Point Name: ACDIN.AH4.SAD3
Point Type: LDO
Descriptor: AH4 SA DPR3
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 09 01
Inverted: No
Point System Name: ACDIN.AH4.SAD4
Point Name: ACDIN.AH4.SAD4
Point Type: LDO
Descriptor: AH4 SA DPR4
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 09 02
Inverted: No
Point System Name: ACDIN.AH4.SAH
Point Name: ACDIN.AH4.SAH
Point Type: LAI
Descriptor: AH4 SA HUMID
Value: 3.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 1.0
Point System Name: ACDIN.AH4.SAS
Point Name: ACDIN.AH4.SAS
Point Type: LAO
Descriptor: SPLY TEMP SETPT
Value: 65.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.SAT
Point Name: ACDIN.AH4.SAT
Point Type: LAI
Descriptor: AH4 SA TEMP
Value: 64.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 15 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
Point System Name: ACDIN.AH4.SFNVFD
Point Name: ACDIN.AH4.SFNVFD
Point Type: LAO
Descriptor: AH4 SFN VFD
Value: 7.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 21 05
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.SHS
Point Name: ACDIN.AH4.SHS
Point Type: LAO
Descriptor: SUP HUM STPT
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH4.SMK
Point Name: ACDIN.AH4.SMK
Point Type: LDI
Descriptor: AH4 SMK ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 03
Normally Closed: No
Point System Name: ACDIN.CHW.DLT
Point Name: ACDIN.CHW.DLT
Point Type: LAO
Descriptor: DELTA TEMP
Value: 14.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.CHW.DLY
Point Name: ACDIN.CHW.DLY
Point Type: LAO
Descriptor: PREV DAY USEAGE
Value: 54859.83
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.CHW.FLW
Point Name: ACDIN.CHW.FLW
Point Type: LAI
Descriptor: CHW GPM FLOW
Value: 64.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.026448
Intercept: -162.60141
COV Limit: 10.0
Point System Name: ACDIN.CHW.MTD
Point Name: ACDIN.CHW.MTD
Point Type: LAO
Descriptor: MONTH TO DATE
Value: 831676.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.CHW.MTR
Point Name: ACDIN.CHW.MTR
Point Type: LAO
Descriptor: CALCULATED TONS
Value: 51.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: Minutes
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.CHW.PMT
Point Name: ACDIN.CHW.PMT
Point Type: LAO
Descriptor: PREVIUOS MONTH
Value: 2448856.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.CHW.PYR
Point Name: ACDIN.CHW.PYR
Point Type: LAO
Descriptor: PREVIUOS YEAR
Value: 11074076.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.CHW.RP
Point Name: ACDIN.CHW.RP
Point Type: LAI
Descriptor: CHWR PRESS
Value: 230.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008139
Intercept: -50.00141
COV Limit: 5.0
Point System Name: ACDIN.CHW.RPT
Point Name: ACDIN.CHW.RPT
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.CHW.RPT1
Point Name: ACDIN.CHW.RPT1
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.CHW.RT
Point Name: ACDIN.CHW.RT
Point Type: LAI
Descriptor: CHWR TEMP
Value: 61.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 20 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.CHW.SP
Point Name: ACDIN.CHW.SP
Point Type: LAI
Descriptor: CHWS PRESS
Value: -0.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008139
Intercept: -50.00141
COV Limit: 5.0
Point System Name: ACDIN.CHW.ST
Point Name: ACDIN.CHW.ST
Point Type: LAI
Descriptor: CHWS TEMP
Value: 47.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 20 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.CHW.YTD
Point Name: ACDIN.CHW.YTD
Point Type: LAO
Descriptor: YEAR TO DATE
Value: 14528966.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.CUH.RMT
Point Name: ACDIN.CUH.RMT
Point Type: LAI
Descriptor: CUH1 RM TEMP
Value: 70.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.CUH1.FRZ
Point Name: ACDIN.CUH1.FRZ
Point Type: LDI
Descriptor: CUH1 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 11
Normally Closed: No
Point System Name: ACDIN.CUH2.RMT
Point Name: ACDIN.CUH2.RMT
Point Type: LAI
Descriptor: CUH2 RM TEMP
Value: 73.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.CUH3.FRZ
Point Name: ACDIN.CUH3.FRZ
Point Type: LDI
Descriptor: CUH3 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 12
Normally Closed: No
Point System Name: ACDIN.CUH3.RMT
Point Name: ACDIN.CUH3.RMT
Point Type: LAI
Descriptor: CUH3 RM TEMP
Value: 69.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.CUH4.RMT
Point Name: ACDIN.CUH4.RMT
Point Type: LAI
Descriptor: CUH4 RM TEMP
Value: 74.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 20 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.DH2O.DLY
Point Name: ACDIN.DH2O.DLY
Point Type: LAO
Descriptor: PREV DAY USEAGE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.DH2O.MTD
Point Name: ACDIN.DH2O.MTD
Point Type: LAO
Descriptor: MONTH TO DATE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.DH2O.MTR
Point Name: ACDIN.DH2O.MTR
Point Type: LPACI
Descriptor: DOM H2O METER
Value: 791703744.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 08
Gain: 100.0
Count Both Edges: No
COV Limit: 1000.0
Point System Name: ACDIN.DH2O.PDY
Point Name: ACDIN.DH2O.PDY
Point Type: LAO
Descriptor: PREV DAY METER
Value: 791703744.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.DH2O.PMT
Point Name: ACDIN.DH2O.PMT
Point Type: LAO
Descriptor: PREVIUOS MONTH
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.DH2O.PYR
Point Name: ACDIN.DH2O.PYR
Point Type: LAO
Descriptor: PREVIUOS YEAR
Value: 802600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.DH2O.RPT
Point Name: ACDIN.DH2O.RPT
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.DH2O.RPT1
Point Name: ACDIN.DH2O.RPT1
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.DH2O.YTD
Point Name: ACDIN.DH2O.YTD
Point Type: LAO
Descriptor: YEAR TO DATE
Value: 785049600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF1
Point Name: ACDIN.EF1
Point Type: L2SL
Descriptor: EF1 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 08 05
Inverted: No
Proof Point Address: 0 10 06
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: ACDIN.EF10
Point Name: ACDIN.EF10
Point Type: L2SL
Descriptor: EF10 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 09 05
Inverted: No
Proof Point Address: 0 11 07
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: ACDIN.EF12
Point Name: ACDIN.EF12
Point Type: L2SL
Descriptor: EF12 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 08 01
Inverted: No
Proof Point Address: 0 11 08
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: ACDIN.EF12.PROOF
Point Name: ACDIN.EF12.PROOF
Point Type: LDI
Descriptor: EF CURRNT PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 08
Normally Closed: No
Point System Name: ACDIN.EF12SW
Point Name: ACDIN.EF12SW
Point Type: LDI
Descriptor: ON OFF SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 16
Normally Closed: No
Point System Name: ACDIN.EF2
Point Name: ACDIN.EF2
Point Type: L2SL
Descriptor: EF2 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 08 04
Inverted: No
Proof Point Address: 0 10 07
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: ACDIN.EF2.PROOF
Point Name: ACDIN.EF2.PROOF
Point Type: LDI
Descriptor: EF CURRNT PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 07
Normally Closed: No
Point System Name: ACDIN.EF2SW
Point Name: ACDIN.EF2SW
Point Type: LDI
Descriptor: ON OFF SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 13
Normally Closed: No
Point System Name: ACDIN.EF3
Point Name: ACDIN.EF3
Point Type: L2SL
Descriptor: EF3 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 08 06
Inverted: No
Proof Point Address: 0 10 08
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: ACDIN.EF3.PROOF
Point Name: ACDIN.EF3.PROOF
Point Type: LDI
Descriptor: EF CURRNT PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 08
Normally Closed: No
Point System Name: ACDIN.EF3SW
Point Name: ACDIN.EF3SW
Point Type: LDI
Descriptor: ON OFF SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 14
Normally Closed: No
Point System Name: ACDIN.EF4
Point Name: ACDIN.EF4
Point Type: L2SL
Descriptor: EF4 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 09 04
Inverted: No
Proof Point Address: 0 11 05
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: ACDIN.EF4.PROOF
Point Name: ACDIN.EF4.PROOF
Point Type: LDI
Descriptor: EF CURRNT PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 05
Normally Closed: No
Point System Name: ACDIN.EF4SW
Point Name: ACDIN.EF4SW
Point Type: LDI
Descriptor: ON OFF SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 15
Normally Closed: No
Point System Name: ACDIN.EF9
Point Name: ACDIN.EF9
Point Type: L2SL
Descriptor: EF9 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 09 06
Inverted: No
Proof Point Address: 0 11 06
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: ACDIN.ELEC
Point Name: ACDIN.ELEC
Point Type: LPACI
Descriptor: ACDIN SHARK ELEC
Value: 202538.2813
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Gain: 0.0
Count Both Edges: No
COV Limit: 1.0
Point System Name: ACDIN.ELEC.METER
Point Name: ACDIN.ELEC.METER
Point Type: LPACI
Descriptor: ACDIN SHARK ELEC
Value: 202538.2813
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 20 06
Gain: 0.24055
Count Both Edges: Yes
COV Limit: 1.0
Point System Name: ACDIN.EMGPWR
Point Name: ACDIN.EMGPWR
Point Type: LDI
Descriptor: EMERG POWER
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 10
Normally Closed: No
Point System Name: ACDIN.FIREALM
Point Name: ACDIN.FIREALM
Point Type: LDI
Descriptor: FIRE ALM GEN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 11 09
Normally Closed: Yes
Point System Name: ACDIN.FRZR1.RMT
Point Name: ACDIN.FRZR1.RMT
Point Type: LAI
Descriptor: FRZR1 RM TEMP
Value: -2.42
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 30.0
Low Limit: -35.0
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 13 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.005859
Intercept: -76.0
COV Limit: 5.0
Point System Name: ACDIN.FRZR2.RMT
Point Name: ACDIN.cooler2.RMT
Point Type: LAI
Descriptor: cooler2 RM TEMP
Value: 40.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 60.0
Low Limit: 20.0
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.005859
Intercept: -76.0
COV Limit: 5.0
Point System Name: ACDIN.FRZR3.RMT
Point Name: ACDIN.FRZR3.RMT
Point Type: LAI
Descriptor: cooler3 RM TEMP
Value: 41.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 55.0
Low Limit: 20.0
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.005859
Intercept: -76.0
COV Limit: 5.0
Point System Name: ACDIN.HUH1.RMT
Point Name: ACDIN.HUH1.RMT
Point Type: LAI
Descriptor: HUH1 RM TEMP
Value: 80.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 20 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.HUH2.RMT
Point Name: ACDIN.HUH2.RMT
Point Type: LAI
Descriptor: CUH2 RM TMP
Value: 63.46
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 55.0
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 20 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
Point System Name: ACDIN.HUH3.RMT
Point Name: ACDIN.HUH3.RMT
Point Type: LAI
Descriptor: HUH3 RM TEMP
Value: 73.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 55.0
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.HX1.HWCS
Point Name: ACDIN.HX1.HWCS
Point Type: LAO
Descriptor: SPLY WATER SETPT
Value: 140.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX1.HWCV
Point Name: ACDIN.HX1.HWCV
Point Type: LAO
Descriptor: LOOP OUTPUT
Value: 88.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX1.HWDP
Point Name: ACDIN.HX1.HWDP
Point Type: LAI
Descriptor: HX1 HW DP
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 15 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.001017
Intercept: -6.25011
COV Limit: 0.5
Point System Name: ACDIN.HX1.HWPLP
Point Name: ACDIN.HX1.HWPLP
Point Type: LAO
Descriptor: PMP SPEED LOOP
Value: 46.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX1.HWRP
Point Name: ACDIN.HX1.HWRP
Point Type: LAI
Descriptor: HX1 HWR PRESS
Value: 7.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 15 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.002035
Intercept: -12.49993
COV Limit: 1.0
Point System Name: ACDIN.HX1.HWRT
Point Name: ACDIN.HX1.HWRT
Point Type: LAI
Descriptor: HX1 HWR TEMP
Value: 131.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
Point System Name: ACDIN.HX1.HWSP
Point Name: ACDIN.HX1.HWSP
Point Type: LAI
Descriptor: HX1 HWS PRESS
Value: 2.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 15 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.002035
Intercept: -12.49993
COV Limit: 1.0
Point System Name: ACDIN.HX1.HWST
Point Name: ACDIN.HX1.HWST
Point Type: LAI
Descriptor: HX1 HWS TEMP
Value: 140.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 15 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
Point System Name: ACDIN.HX1.LD
Point Name: ACDIN.HX1.LD
Point Type: LDO
Descriptor: PUMP LEAD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.HX1.LD1
Point Name: ACDIN.HX1.LD1
Point Type: LDO
Descriptor: LEAD LAG 1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.HX1.LD2
Point Name: ACDIN.HX1.LD2
Point Type: LDO
Descriptor: LEAD LAG 2
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.HX1.PP1
Point Name: ACDIN.HX1.PP1
Point Type: L2SL
Descriptor: HX1 PMP1 SS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 09 03
Inverted: Yes
Proof Point Address: 0 10 13
Normally Closed: No
Proof Delay: 120 Informational Text
Point System Name: ACDIN.HX1.PP1VFD
Point Name: ACDIN.HX1.PP1VFD
Point Type: LAO
Descriptor: HX1 PMP1 VFD
Value: 4.68
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 21 03
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX1.PP2
Point Name: ACDIN.HX1.PP2
Point Type: L2SL
Descriptor: HX1 PMP2 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 07 04
Inverted: Yes
Proof Point Address: 0 10 14
Normally Closed: No
Proof Delay: 120 Informational Text
Point System Name: ACDIN.HX1.PP2VFD
Point Name: ACDIN.HX1.PP2VFD
Point Type: LAO
Descriptor: HX1 PMP2 VFD
Value: 4.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 21 04
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX1.VLV1
Point Name: ACDIN.HX1.VLV1
Point Type: LAO
Descriptor: HX1 VLV 1
Value: 10.47
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 02 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX1.VLV2
Point Name: ACDIN.HX1.VLV2
Point Type: LAO
Descriptor: HX1 VLV 2
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 02 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX3.DBO
Point Name: ACDIN.HX3.DBO
Point Type: LAO
Descriptor: SETPNT OFFSET
Value: 125.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX3.HWRT
Point Name: ACDIN.HX3.HWRT
Point Type: LAI
Descriptor: HX3 HWR TEMP
Value: 122.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
Point System Name: ACDIN.HX3.HWSSP
Point Name: ACDIN.HX3.HWSSP
Point Type: LAO
Descriptor: CONV SPLY SETPT
Value: 125.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX3.HWST
Point Name: ACDIN.HX3.HWST
Point Type: LAI
Descriptor: CONV SPLY TEMP
Value: 125.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
Point System Name: ACDIN.HX3.HWTSP
Point Name: ACDIN.HX3.HWTSP
Point Type: LAO
Descriptor: DOM TANK SETPNT
Value: 120.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX3.P3O
Point Name: ACDIN.HX3.P3O
Point Type: LDO
Descriptor: P3 OFF POINT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.HX3.PP3
Point Name: ACDIN.HX3.PP3
Point Type: L2SL
Descriptor: HX3 PMP3 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 07 05
Inverted: No
Proof Point Address: 0 10 15
Normally Closed: No
Proof Delay: 10 Informational Text
Point System Name: ACDIN.HX3.PP4
Point Name: ACDIN.HX3.PP4
Point Type: L2SL
Descriptor: HX3 PMP4 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
On/Off Point Address: 0 07 06
Inverted: No
Proof Point Address: 0 10 16
Normally Closed: No
Proof Delay: 10 Informational Text
Point System Name: ACDIN.HX3.TNKTMP
Point Name: ACDIN.HX3.TNKTMP
Point Type: LAI
Descriptor: HX3 TANK TMP
Value: 123.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 19 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 5.0
Point System Name: ACDIN.HX3.VLV1
Point Name: ACDIN.HX3.VLV1
Point Type: LAO
Descriptor: HX3 VLV 1
Value: 3.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 02 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX3.VLV2
Point Name: ACDIN.HX3.VLV2
Point Type: LAO
Descriptor: HX3 VLV 2
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 02 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HX3.XVO
Point Name: ACDIN.HX3.XVO
Point Type: LAO
Descriptor: CONV LOOP OUTPUT
Value: 15.55
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.KITCHEN.ZON:MODE
Point Name: ACDIN.KITCHEN.ZON:MODE
Point Type: LENUM
Descriptor: KITCHEN AREA
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.LOUNGE.ZON:MODE
Point Name: ACDIN.LOUNGE.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.MAINDINE.ZON:MODE
Point Name: ACDIN.MAINDINE.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.MBC43.TEC.COMMANDS:PPCL Address
Point Name: ACDIN.MBC43.TEC.COMMANDS:PPCL Address
Point Type: LAI
Descriptor:
Value: 43
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: ACDIN.OFFICE.KTCHN.ZON:MODE
Point Name: ACDIN.OFFICE.KTCHN.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.PNL43.SHEDTMR
Point Name: ACDIN.PNL43.SHEDTMR
Point Type: LAO
Descriptor: MBC43 SHED TIMER
Value: 41482916.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.RAD001:DAY.NGT
Point Name: ACDIN.RAD001:DAY.NGT
Point Type: LDO
Descriptor: RM104 RAD
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 06 29
Inverted: No
Point System Name: ACDIN.RAD001.HEAT COOL
Point Name: ACDIN.RAD001.HEAT COOL
Point Type: LDO
Descriptor: HEAT COOL SWITCH
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 06 05
Inverted: No
Point System Name: ACDIN.RAD001.HTG LOOPOUT
Point Name: ACDIN.RAD001.HTG LOOPOUT
Point Type: LAO
Descriptor: HEATING LOOP
Value: 3
Condition: -N-
Priority: OVRD
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 06 80
Actuator Type Voltage
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.RAD002:DAY.NGT
Point Name: ACDIN.RAD002:DAY.NGT
Point Type: LDO
Descriptor: RM105 RAD
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 13 29
Inverted: No
Point System Name: ACDIN.RAD003:DAY.NGT
Point Name: ACDIN.RAD003:DAY.NGT
Point Type: LDO
Descriptor: RM109 RAD
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 04 29
Inverted: No
Point System Name: ACDIN.RAD004:DAY.NGT
Point Name: ACDIN.RAD004:DAY.NGT
Point Type: LDO
Descriptor: RM126 RAD
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 03 29
Inverted: No
Point System Name: ACDIN.RAD005:DAY.NGT
Point Name: ACDIN.RAD005:DAY.NGT
Point Type: LDO
Descriptor: RM127 RAD
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 02 29
Inverted: No
Point System Name: ACDIN.RAD006:DAY.NGT
Point Name: ACDIN.RAD006:DAY.NGT
Point Type: LDO
Descriptor: RAD RM128
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 25 29
Inverted: No
Point System Name: ACDIN.RM104.ZON:MODE
Point Name: ACDIN.RM104.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.S51DINNING:MODE
Point Name: ACDIN.S51DINNING:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.SERVERY.ZON:MODE
Point Name: ACDIN.SERVERY.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.SHEARERDINNING:MODE
Point Name: ACDIN.SHEARERDINNING:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.STEAM.DLY
Point Name: ACDIN.STEAM.DLY
Point Type: LAO
Descriptor: PREV DAY USEAGE
Value: 27683.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.STEAM.FLOW
Point Name: ACDIN.STEAM.FLOW
Point Type: LAI
Descriptor: STEAM LBS HR
Value: 5.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: LB HR
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM43
Point Address: 0 15 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.406901
Intercept: -2500.0
COV Limit: 0.5
Point System Name: ACDIN.STEAM.HIPRS
Point Name: ACDIN.STEAM.HIPRS
Point Type: LAI
Descriptor: HP STM PRESS
Value: 79.07
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 50.0
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.006104
Intercept: -37.5
COV Limit: 5.0
Point System Name: ACDIN.STEAM.LOPRS
Point Name: ACDIN.STEAM.LOPRS
Point Type: LAI
Descriptor: LP STM PRESS
Value: 10.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Standard Alarms
High Limit: 15.0
Low Limit: 5.0
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 14 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000814
Intercept: -5.0
COV Limit: 0.5
Point System Name: ACDIN.STEAM.MTD
Point Name: ACDIN.STEAM.MTD
Point Type: LAO
Descriptor: MONTH TO DATE
Value: 222830.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.STEAM.PMT
Point Name: ACDIN.STEAM.PMT
Point Type: LAO
Descriptor: PREVIUOS MONTH
Value: 199130.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.STEAM.PYR
Point Name: ACDIN.STEAM.PYR
Point Type: LAO
Descriptor: PREVIUOS YEAR
Value: 6249368.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.STEAM.RPT
Point Name: ACDIN.STEAM.RPT
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.STEAM.RPT1
Point Name: ACDIN.STEAM.RPT1
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.STEAM.YTD
Point Name: ACDIN.STEAM.YTD
Point Type: LAO
Descriptor: YEAR TO DATE
Value: 5349369.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.SUMP.CP1ALM
Point Name: ACDIN.SUMP.CP1ALM
Point Type: LDI
Descriptor: SUMP CP1 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 09
Normally Closed: No
Point System Name: ACDIN.SUMP.CP2ALM
Point Name: ACDIN.SUMP.CP2ALM
Point Type: LDI
Descriptor: SUMP CP2 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 10
Normally Closed: No
Point System Name: ACDIN.SUMP.CP3ALM
Point Name: ACDIN.SUMP.CP3ALM
Point Type: LDI
Descriptor: SUMP CP3 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 11
Normally Closed: No
Point System Name: ACDIN.SUMP.ELEVALM
Point Name: ACDIN.SUMP.ELEVALM
Point Type: LDI
Descriptor: ELEV SUMP ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 0 10 12
Normally Closed: No
Point System Name: ACDIN.TOILET.EXH.ZON:MODE
Point Name: ACDIN.TOILET.EXH.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Point System Name: ACDIN.VAV001:DAY.NGT
Point Name: ACDIN.VAV001:DAY.NGT
Point Type: LDO
Descriptor: RM113 VAV001
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 14 29
Inverted: No
Point System Name: ACDIN.VAV001.CTLFLMN
Point Name: ACDIN.VAV001.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 500.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 14 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV001.ORGSTPT
Point Name: ACDIN.VAV001.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV002:DAY.NGT
Point Name: ACDIN.VAV002:DAY.NGT
Point Type: LDO
Descriptor: RM115 VAV002
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 15 29
Inverted: No
Point System Name: ACDIN.VAV002.CTLFLMN
Point Name: ACDIN.VAV002.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 524.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 15 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV002.ORGSTPT
Point Name: ACDIN.VAV002.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV003:DAY.NGT
Point Name: ACDIN.VAV003:DAY.NGT
Point Type: LDO
Descriptor: RM117 VAV003
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 16 29
Inverted: No
Point System Name: ACDIN.VAV003.CTLFLMN
Point Name: ACDIN.VAV003.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 936.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 16 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV003.ORGSTPT
Point Name: ACDIN.VAV003.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV004:DAY.NGT
Point Name: ACDIN.VAV004:DAY.NGT
Point Type: LDO
Descriptor: VAV004 RM111
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 17 29
Inverted: No
Point System Name: ACDIN.VAV004.CTLFLMN
Point Name: ACDIN.VAV004.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 17 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV004.ORGSTPT
Point Name: ACDIN.VAV004.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV005:DAY.NGT
Point Name: ACDIN.VAV005:DAY.NGT
Point Type: LDO
Descriptor: VAV005 RM111
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 18 29
Inverted: No
Point System Name: ACDIN.VAV005.CTLFLMN
Point Name: ACDIN.VAV005.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 576.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 18 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV005.ORGSTPT
Point Name: ACDIN.VAV005.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV006:DAY.NGT
Point Name: ACDIN.VAV006:DAY.NGT
Point Type: LDO
Descriptor: RM111 VAV006
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 11 29
Inverted: No
Point System Name: ACDIN.VAV006.CTLFLMN
Point Name: ACDIN.VAV006.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 11 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV006.ORGSTPT
Point Name: ACDIN.VAV006.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV007:DAY.NGT
Point Name: ACDIN.VAV007:DAY.NGT
Point Type: LDO
Descriptor: RM112 VAV007
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 12 29
Inverted: No
Point System Name: ACDIN.VAV007.CTLFLMN
Point Name: ACDIN.VAV007.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 1476.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 12 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV007.ORGSTPT
Point Name: ACDIN.VAV007.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV009:DAY.NGT
Point Name: ACDIN.VAV009:DAY.NGT
Point Type: LDO
Descriptor: RM111 VAV009
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 10 29
Inverted: No
Point System Name: ACDIN.VAV009.CTLFLMN
Point Name: ACDIN.VAV009.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 252.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV009.ORGSTPT
Point Name: ACDIN.VAV009.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV010:DAY.NGT
Point Name: ACDIN.VAV010:DAY.NGT
Point Type: LDO
Descriptor: VAV010 RM110
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 19 29
Inverted: No
Point System Name: ACDIN.VAV010.CTLFLMN
Point Name: ACDIN.VAV010.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 800.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 19 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV010.ORGSTPT
Point Name: ACDIN.VAV010.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV011:DAY.NGT
Point Name: ACDIN.VAV011:DAY.NGT
Point Type: LDO
Descriptor: VAV011 RM110
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 20 29
Inverted: No
Point System Name: ACDIN.VAV011.CTLFLMN
Point Name: ACDIN.VAV011.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 20 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV011.ORGSTPT
Point Name: ACDIN.VAV011.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV012:DAY.NGT
Point Name: ACDIN.VAV012:DAY.NGT
Point Type: LDO
Descriptor: VAV012 RM122
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 21 29
Inverted: No
Point System Name: ACDIN.VAV012.CTLFLMN
Point Name: ACDIN.VAV012.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 21 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV012.ORGSTPT
Point Name: ACDIN.VAV012.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV013:DAY.NGT
Point Name: ACDIN.VAV013:DAY.NGT
Point Type: LDO
Descriptor: VAV013 RM118
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 22 29
Inverted: No
Point System Name: ACDIN.VAV013.CTLFLMN
Point Name: ACDIN.VAV013.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 22 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV013.ORGSTPT
Point Name: ACDIN.VAV013.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV014:DAY.NGT
Point Name: ACDIN.VAV014:DAY.NGT
Point Type: LDO
Descriptor: RM103 VAV014
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 09 29
Inverted: No
Point System Name: ACDIN.VAV014.CTLFLMN
Point Name: ACDIN.VAV014.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 09 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV014.ORGSTPT
Point Name: ACDIN.VAV014.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV015:DAY.NGT
Point Name: ACDIN.VAV015:DAY.NGT
Point Type: LDO
Descriptor: RM104 VAV015
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 07 29
Inverted: No
Point System Name: ACDIN.VAV015.CLG LOOPOUT
Point Name: ACDIN.VAV015.CLG LOOPOUT
Point Type: LAI
Descriptor: COOLING LOOP
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 07 79
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV015.CTLFLMN
Point Name: ACDIN.VAV015.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV015.HEAT COOL
Point Name: ACDIN.VAV015.HEAT COOL
Point Type: LDI
Descriptor: HEAT COOL SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 07 05
Normally Closed: No
Point System Name: ACDIN.VAV015.HTG LOOPOUT
Point Name: ACDIN.VAV015.HTG LOOPOUT
Point Type: LAI
Descriptor: HEATING LOOP
Value: 3
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 07 80
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV015.ORGSTPT
Point Name: ACDIN.VAV015.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV016:DAY.NGT
Point Name: ACDIN.VAV016:DAY.NGT
Point Type: LDO
Descriptor: RM104 VAV016
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 08 29
Inverted: No
Point System Name: ACDIN.VAV016.CLG LOOPOUT
Point Name: ACDIN.VAV016.CLG LOOPOUT
Point Type: LAO
Descriptor: COOLING LOOP
Value: 0
Condition: -N-
Priority: OVRD
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 08 79
Actuator Type Voltage
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV016.CTLFLMN
Point Name: ACDIN.VAV016.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 352.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 08 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV016.HEAT COOL
Point Name: ACDIN.VAV016.HEAT COOL
Point Type: LDO
Descriptor: HEAT COOL SWITCH
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 08 05
Inverted: No
Point System Name: ACDIN.VAV016.HTG LOOPOUT
Point Name: ACDIN.VAV016.HTG LOOPOUT
Point Type: LAO
Descriptor: HEATING LOOP
Value: 3
Condition: -N-
Priority: OVRD
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 08 80
Actuator Type Voltage
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV016.ORGSTPT
Point Name: ACDIN.VAV016.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV017:DAY.NGT
Point Name: ACDIN.VAV017:DAY.NGT
Point Type: LDO
Descriptor: RM108 VAV017
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 05 29
Inverted: No
Point System Name: ACDIN.VAV017.CTLFLMN
Point Name: ACDIN.VAV017.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 220.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV017.ORGSTPT
Point Name: ACDIN.VAV017.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV018:DAY.NGT
Point Name: ACDIN.VAV018:DAY.NGT
Point Type: LDO
Descriptor: VAV018 RM123
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 23 29
Inverted: No
Point System Name: ACDIN.VAV018.CTLFLMN
Point Name: ACDIN.VAV018.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 752.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 23 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV018.ORGSTPT
Point Name: ACDIN.VAV018.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV019:DAY.NGT
Point Name: ACDIN.VAV019:DAY.NGT
Point Type: LDO
Descriptor: VAV019 RM132
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 24 29
Inverted: No
Point System Name: ACDIN.VAV019.CTLFLMN
Point Name: ACDIN.VAV019.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 252.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV019.ORGSTPT
Point Name: ACDIN.VAV019.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV020:DAY.NGT
Point Name: ACDIN.VAV020:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 01 29
Inverted: No
Point System Name: ACDIN.VAV020.CTLFLMN
Point Name: ACDIN.VAV020.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 120.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: 1 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV020.ORGSTPT
Point Name: ACDIN.VAV020.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM43
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.2FLRHALLWAY.ZON:MODE
Point Name: ACDIN.2FLRHALLWAY.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.3FLRHALLWAY.ZON:MODE
Point Name: ACDIN.3FLRHALLWAY.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH2.CCV
Point Name: ACDIN.AH2.CCV
Point Type: LAO
Descriptor: AH2 CLG VLV
Value: 8.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.CO2OA
Point Name: ACDIN.AH2.CO2OA
Point Type: LAI
Descriptor: AH2 OA CO2 PPM
Value: -246.13
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PPM CO
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.08138
Intercept: -500.0
COV Limit: 10.0
Point System Name: ACDIN.AH2.CO2RA
Point Name: ACDIN.AH2.CO2RA
Point Type: LAI
Descriptor: AH2 RA CO2 PPM
Value: -293.5
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PPM CO
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.08138
Intercept: -500.0
COV Limit: 10.0
Point System Name: ACDIN.AH2.DBS
Point Name: ACDIN.AH2.DBS
Point Type: LAO
Descriptor: ECONOMIZE SWITCH
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.DSP
Point Name: ACDIN.AH2.DSP
Point Type: LAO
Descriptor: DUCT STATIC PRES
Value: 1.2432
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.05
Point System Name: ACDIN.AH2.DSP1
Point Name: ACDIN.AH2.DSP1
Point Type: LAI
Descriptor: AH2 SA PRS1
Value: 1.2803
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24996
COV Limit: 0.05
Point System Name: ACDIN.AH2.DSP2
Point Name: ACDIN.AH2.DSP2
Point Type: LAI
Descriptor: AH2 SA PRS2
Value: 1.236
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24996
COV Limit: 0.05
Point System Name: ACDIN.AH2.DSSP
Point Name: ACDIN.AH2.DSSP
Point Type: LAO
Descriptor: DUCT STATIC STPT
Value: 1.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.005
Point System Name: ACDIN.AH2.ECN
Point Name: ACDIN.AH2.ECN
Point Type: LDO
Descriptor: ECONOMIZE MODE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH2.ERR
Point Name: ACDIN.AH2.ERR
Point Type: LAO
Descriptor: SPLY TEMP ERROR
Value: 1.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.FBD
Point Name: ACDIN.AH2.FBD
Point Type: LAO
Descriptor: AH2 FB DMPRS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.FRZ
Point Name: ACDIN.AH2.FRZ
Point Type: LDI
Descriptor: AH2 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM44
Point Address: 0 11 03
Normally Closed: No
Point System Name: ACDIN.AH2.HCV
Point Name: ACDIN.AH2.HCV
Point Type: LAO
Descriptor: AH2 HTG VLV
Value: 18.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.HFBS
Point Name: ACDIN.AH2.HFBS
Point Type: LDO
Descriptor: HTG F/B SWITCH
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH2.HSP
Point Name: ACDIN.AH2.HSP
Point Type: LDI
Descriptor: AH2 HI STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 11 05
Normally Closed: Yes
Point System Name: ACDIN.AH2.LP1
Point Name: ACDIN.AH2.LP1
Point Type: LAO
Descriptor: MIX AIR LOOPOUT
Value: 76.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.LP2
Point Name: ACDIN.AH2.LP2
Point Type: LAO
Descriptor: RET FAN RESET
Value: 5.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.LPO
Point Name: ACDIN.AH2.LPO
Point Type: LAO
Descriptor: SUP TEMP LOOPOUT
Value: 84.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.MAD
Point Name: ACDIN.AH2.MAD
Point Type: LAO
Descriptor: AH2 MA DMPRS
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.MAM
Point Name: ACDIN.AH2.MAM
Point Type: LAO
Descriptor: MIN DPR POS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.MAS
Point Name: ACDIN.AH2.MAS
Point Type: LAO
Descriptor: MIX AIR SETPNT
Value: 55.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.MAT
Point Name: ACDIN.AH2.MAT
Point Type: LAI
Descriptor: AH2 MA TEMP
Value: 65.55
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.MAX.DMPR.COMD
Point Name: ACDIN.AH2.MAX.DMPR.COMD
Point Type: LAO
Descriptor: MAX VAV DMPR
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: %
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.MOAD
Point Name: ACDIN.AH2.MOAD
Point Type: LAO
Descriptor: AH2 MAX OAD
Value: 16.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.MOD
Point Name: ACDIN.AH2.MOD
Point Type: LAO
Descriptor: AH2 MODE
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.NMBR.REQ.CLG
Point Name: ACDIN.AH2.NMBR.REQ.CLG
Point Type: LAO
Descriptor: NMBR REQ CLG
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UNITS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.OACFM
Point Name: ACDIN.AH2.OACFM
Point Type: LAO
Descriptor: OA CFM
Value: 13677.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 50.0
Point System Name: ACDIN.AH2.OACFMA
Point Name: ACDIN.AH2.OACFMA
Point Type: LAO
Descriptor: AVG OA CFM
Value: 13691.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.OACFMLO
Point Name: ACDIN.AH2.OACFMLO
Point Type: LAO
Descriptor: OA CFM LOOPOUT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.OACFMS
Point Name: ACDIN.AH2.OACFMS
Point Type: LAO
Descriptor: OA CFM STPT
Value: 3000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 50.0
Point System Name: ACDIN.AH2.OAT
Point Name: ACDIN.AH2.OAT
Point Type: LAO
Descriptor: VIR OAT
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.OAVELP
Point Name: ACDIN.AH2.OAVELP
Point Type: LAI
Descriptor: AH2 OA VEL PRESS
Value: 1141.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 10 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.203451
Intercept: -1250.0
COV Limit: 10.0
Point System Name: ACDIN.AH2.OAVELPA
Point Name: ACDIN.AH2.OAVELPA
Point Type: LAO
Descriptor: AVG OA VEL PRESS
Value: 1141.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
Point System Name: ACDIN.AH2.OCC
Point Name: ACDIN.AH2.OCC
Point Type: LDO
Descriptor: OCC MODE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH2.RADPT
Point Name: ACDIN.AH2.RADPT
Point Type: LAO
Descriptor: RTRN DEW POINT
Value: 38.59
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.RAH
Point Name: ACDIN.AH2.RAH
Point Type: LAI
Descriptor: AH2 RA HUMID
Value: 30.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 10 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 3.0
Point System Name: ACDIN.AH2.RAT
Point Name: ACDIN.AH2.RAT
Point Type: LAI
Descriptor: AH2 RA TEMP
Value: 71.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.AH2.RDPS
Point Name: ACDIN.AH2.RDPS
Point Type: LAO
Descriptor: CL DN SPLY SETPT
Value: 53.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.RFN
Point Name: ACDIN.AH2.RFN
Point Type: L2SL
Descriptor: AH2 RFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM44
On/Off Point Address: 0 07 02
Inverted: No
Proof Point Address: 0 11 02
Normally Closed: No
Proof Delay: 90 Informational Text
Point System Name: ACDIN.AH2.RFNVFD
Point Name: ACDIN.AH2.RFNVFD
Point Type: LAO
Descriptor: AH2 RFN VFD
Value: 5.21
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 02 02
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.SAS
Point Name: ACDIN.AH2.SAS
Point Type: LAO
Descriptor: SUPPLY AIR SETPT
Value: 63.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.SAT
Point Name: ACDIN.AH2.SAT
Point Type: LAI
Descriptor: AH2 SA TEMP
Value: 64.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.SFN
Point Name: ACDIN.AH2.SFN
Point Type: L2SL
Descriptor: AH2 SFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM44
On/Off Point Address: 0 07 01
Inverted: No
Proof Point Address: 0 11 01
Normally Closed: No
Proof Delay: 90 Informational Text
Point System Name: ACDIN.AH2.SFNVFD
Point Name: ACDIN.AH2.SFNVFD
Point Type: LAO
Descriptor: AH2 SFN VFD
Value: 6.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 02 03
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.SMK
Point Name: ACDIN.AH2.SMK
Point Type: LDI
Descriptor: AH2 SMK ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 11 04
Normally Closed: No
Point System Name: ACDIN.AH2.SP1
Point Name: ACDIN.AH2.SP1
Point Type: LAO
Descriptor: SPLY STATIC RAMP
Value: 1.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.SSP
Point Name: ACDIN.AH2.SSP
Point Type: LAI
Descriptor: AH2. RM PRESS
Value: 0.0396
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 10 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: -0.37491
COV Limit: 0.01
Point System Name: ACDIN.AH2.T01
Point Name: ACDIN.AH2.T01
Point Type: LAO
Descriptor: SPLY SETPT TIMER
Value: 29195.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: SECS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.T04
Point Name: ACDIN.AH2.T04
Point Type: LAO
Descriptor: SPLY SPD TIMER
Value: 29195.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: SECS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.T05
Point Name: ACDIN.AH2.T05
Point Type: LAO
Descriptor: RTRN SPD TIMER
Value: 29185.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: SECS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.TIME.DELAY
Point Name: ACDIN.AH2.TIME.DELAY
Point Type: LDO
Descriptor: TD PRIOR TO OCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH2.TLTS
Point Name: ACDIN.AH2.TLTS
Point Type: LAO
Descriptor: TIME TIL STARTUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH2.WCF
Point Name: ACDIN.AH2.WCF
Point Type: LDO
Descriptor: WUP WCD SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH3.CCV
Point Name: ACDIN.AH3.CCV
Point Type: LAO
Descriptor: AH3 CLG VLV
Value: 9.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 08
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.DSSP
Point Name: ACDIN.AH3.DSSP
Point Type: LAO
Descriptor: DUCT STATC SETPT
Value: -0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
Point System Name: ACDIN.AH3.EPRFN
Point Name: ACDIN.AH3.EPRFN
Point Type: L2SL
Descriptor: AH3 RFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM44
On/Off Point Address: 0 08 01
Inverted: No
Proof Point Address: 0 11 08
Normally Closed: No
Proof Delay: 20 Informational Text
Point System Name: ACDIN.AH3.EPSFN
Point Name: ACDIN.AH3.EPSFN
Point Type: L2SL
Descriptor: AH3 SFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM44
On/Off Point Address: 0 07 03
Inverted: No
Proof Point Address: 0 11 07
Normally Closed: No
Proof Delay: 20 Informational Text
Point System Name: ACDIN.AH3.FBD
Point Name: ACDIN.AH3.FBD
Point Type: LAO
Descriptor: AH3 FB DMPRS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.FBSW
Point Name: ACDIN.AH3.FBSW
Point Type: LDO
Descriptor: VIRT.ON/OFF. FBD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH3.FRZ
Point Name: ACDIN.AH3.FRZ
Point Type: LDI
Descriptor: AH3 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 11 09
Normally Closed: No
Point System Name: ACDIN.AH3.HCV
Point Name: ACDIN.AH3.HCV
Point Type: LAO
Descriptor: AH3 HTG VLV
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 01 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.HSP
Point Name: ACDIN.AH3.HSP
Point Type: LDI
Descriptor: AH3 HI STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 11 06
Normally Closed: Yes
Point System Name: ACDIN.AH3.HTG
Point Name: ACDIN.AH3.HTG
Point Type: LDO
Descriptor: ON/OFF.HGT.MODE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH3.LPO
Point Name: ACDIN.AH3.LPO
Point Type: LAO
Descriptor: VIRT.LOOPOUTPUT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.MAT
Point Name: ACDIN.AH3.MAT
Point Type: LAI
Descriptor: AH3 MA TEMP
Value: 71.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.AH3.OAT
Point Name: ACDIN.AH3.OAT
Point Type: LAO
Descriptor: VIRT.OUT.AIR
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.OCC
Point Name: ACDIN.AH3.OCC
Point Type: LDO
Descriptor: VIRT.ON/OFF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH3.RAH
Point Name: ACDIN.AH3.RAH
Point Type: LAI
Descriptor: AH3 RA HUMID
Value: 31.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 10 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 3.0
Point System Name: ACDIN.AH3.RAT
Point Name: ACDIN.AH3.RAT
Point Type: LAI
Descriptor: AH3 RA TEMP
Value: 71.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.AH3.RFNVFD
Point Name: ACDIN.AH3.RFNVFD
Point Type: LAO
Descriptor: AH3 RFN VFD
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 02 04
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.RMHZN1
Point Name: ACDIN.AH3.RMHZN1
Point Type: LAI
Descriptor: AH2 RMH ZN1
Value: 19.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Standard Alarms
High Limit: 70.0
Low Limit: 0.0
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 3.0
Point System Name: ACDIN.AH3.RMHZN2
Point Name: ACDIN.AH3.RMHZN2
Point Type: LAI
Descriptor: AH3 RMH ZN2
Value: 21.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Standard Alarms
High Limit: 72.0
Low Limit: 0.0
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 3.0
Point System Name: ACDIN.AH3.SAS
Point Name: ACDIN.AH3.SAS
Point Type: LAO
Descriptor: VIRT.SPLY.SETPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.SAT
Point Name: ACDIN.AH3.SAT
Point Type: LAI
Descriptor: AH3 SA TEMP
Value: 54.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 120.0
Low Limit: 40.0
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.AH3.SMK
Point Name: ACDIN.AH3.SMK
Point Type: LDI
Descriptor: AH3 SMK ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 11 10
Normally Closed: No
Point System Name: ACDIN.AH3.SSP
Point Name: ACDIN.AH3.SSP
Point Type: LAO
Descriptor: VIRT.STAT.MIN
Value: -0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.SSP1
Point Name: ACDIN.AH3.SSP1
Point Type: LAI
Descriptor: AH3 RM PRESS1
Value: 0.002
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 3
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: -0.3725
COV Limit: 0.001
Point System Name: ACDIN.AH3.SSP2
Point Name: ACDIN.AH3.SSP2
Point Type: LAI
Descriptor: AH3 RM PRESS2
Value: -0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 3
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 09 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: -0.375
COV Limit: 0.001
Point System Name: ACDIN.AH3.SSSP
Point Name: ACDIN.AH3.SSSP
Point Type: LAO
Descriptor: VIRT.STAT.PRESS.
Value: -0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.TLTS
Point Name: ACDIN.AH3.TLTS
Point Type: LAO
Descriptor: TIME TIL STARTUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH3.VSFN
Point Name: ACDIN.AH3.VSFN
Point Type: LDO
Descriptor: VIR SPLY FAN
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH4.FBSW
Point Name: ACDIN.AH4.FBSW
Point Type: LDO
Descriptor: VIRT.ON/OFF. FBD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.AH5.RMT
Point Name: ACDIN.AH5.RMT
Point Type: LAI
Descriptor: AH5 RM TEMP
Value: 78.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 02 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.AH5SS
Point Name: ACDIN.AH5SS
Point Type: LDO
Descriptor: AH5 SFN SS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM44
Point Address: 0 08 02
Inverted: No
Point System Name: ACDIN.AH6.FRZ
Point Name: ACDIN.AH6.FRZ
Point Type: LDI
Descriptor: AH6 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 11 12
Normally Closed: No
Point System Name: ACDIN.AH6.MAD
Point Name: ACDIN.AH6.MAD
Point Type: LAO
Descriptor: AH6 MA DMPRS
Value: 11.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 02 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH6.MAS
Point Name: ACDIN.AH6.MAS
Point Type: LAO
Descriptor: VIRT.MIX SETPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH6.MAT
Point Name: ACDIN.AH6.MAT
Point Type: LAI
Descriptor: AH6 MA TEMP
Value: 69.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.AH6.RMS
Point Name: ACDIN.AH6.RMS
Point Type: LAO
Descriptor: VIRT. RM SETPT
Value: 80.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.AH6.RMT
Point Name: ACDIN.AH6.RMT
Point Type: LAI
Descriptor: AH6 RM TEMP
Value: 78.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 03 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
Point System Name: ACDIN.AH6.SFN
Point Name: ACDIN.AH6.SFN
Point Type: L2SL
Descriptor: AH6 SFN SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: ACDIN.PXCM44
On/Off Point Address: 0 07 04
Inverted: No
Proof Point Address: 0 11 11
Normally Closed: No
Proof Delay: 10 Informational Text
Point System Name: ACDIN.AH6.SMK
Point Name: ACDIN.AH6.SMK
Point Type: LDI
Descriptor: AH6 SMK ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 0 11 13
Normally Closed: No
Point System Name: ACDIN.EF8SS
Point Name: ACDIN.EF8SS
Point Type: LDO
Descriptor: EF8 SS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: ACDIN.PXCM44
Point Address: 0 08 03
Inverted: No
Point System Name: ACDIN.MBC44.TEC.COMMANDS:PPCL Address
Point Name: ACDIN.MBC44.TEC.COMMANDS:PPCL Address
Point Type: LAI
Descriptor:
Value: 44
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: ACDIN.PNL44.SHEDTMR
Point Name: ACDIN.PNL44.SHEDTMR
Point Type: LAO
Descriptor: MBC44 SHED TIMER
Value: 20147952.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.RAD007:DAY.NGT
Point Name: ACDIN.RAD007:DAY.NGT
Point Type: LDO
Descriptor: RAD007RM235
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 25 29
Inverted: No
Point System Name: ACDIN.RAD008:DAY.NGT
Point Name: ACDIN.RAD008:DAY.NGT
Point Type: LDO
Descriptor: RAD008RM300
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 25 29
Inverted: No
Point System Name: ACDIN.RAD009:DAY.NGT
Point Name: ACDIN.RAD009:DAY.NGT
Point Type: LDO
Descriptor: RAD009RM301
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 18 29
Inverted: No
Point System Name: ACDIN.RAD009.HEAT COOL
Point Name: ACDIN.RAD009.HEAT COOL
Point Type: LDO
Descriptor: HEAT COOL SWITCH
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 18 05
Inverted: No
Point System Name: ACDIN.RAD009.HTG LOOPOUT
Point Name: ACDIN.RAD009.HTG LOOPOUT
Point Type: LAO
Descriptor: HEATING LOOP
Value: 0
Condition: -N-
Priority: OVRD
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 18 80
Actuator Type Voltage
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.RAD010:DAY.NGT
Point Name: ACDIN.RAD010:DAY.NGT
Point Type: LDO
Descriptor: RAN010RM302
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 21 29
Inverted: No
Point System Name: ACDIN.RAD010.HEAT COOL
Point Name: ACDIN.RAD010.HEAT COOL
Point Type: LDO
Descriptor: HEAT COOL SWITCH
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 21 05
Inverted: No
Point System Name: ACDIN.RAD010.HTG LOOPOUT
Point Name: ACDIN.RAD010.HTG LOOPOUT
Point Type: LAO
Descriptor: HEATING LOOP
Value: 0
Condition: -N-
Priority: OVRD
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 21 80
Actuator Type Voltage
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.RM201.ZON:MODE
Point Name: ACDIN.RM201.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM202.ZON:MODE
Point Name: ACDIN.RM202.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM203.ZON:MODE
Point Name: ACDIN.RM203.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM204.ZON:MODE
Point Name: ACDIN.RM204.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM205.ZON:MODE
Point Name: ACDIN.RM205.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM211.ZON:MODE
Point Name: ACDIN.RM211.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM212.ZON:MODE
Point Name: ACDIN.RM212.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM213.ZON:MODE
Point Name: ACDIN.RM213.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM214.ZON:MODE
Point Name: ACDIN.RM214.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM215.ZON:MODE
Point Name: ACDIN.RM215.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM216.ZON:MODE
Point Name: ACDIN.RM216.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM217.ZON:MODE
Point Name: ACDIN.RM217.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM220.ZON:MODE
Point Name: ACDIN.RM220.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM221.ZON:MODE
Point Name: ACDIN.RM221.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM222.ZON:MODE
Point Name: ACDIN.RM222.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM223.ZON:MODE
Point Name: ACDIN.RM223.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM231.ZON:MODE
Point Name: ACDIN.RM231.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM234.ZON:MODE
Point Name: ACDIN.RM234.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM235.ZON:MODE
Point Name: ACDIN.RM235.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM236.ZON:MODE
Point Name: ACDIN.RM236.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM240.ZON:MODE
Point Name: ACDIN.RM240.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM241.ZON:MODE
Point Name: ACDIN.RM241.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM242.ZON:MODE
Point Name: ACDIN.RM242.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM243.ZON:MODE
Point Name: ACDIN.RM243.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM244.ZON:MODE
Point Name: ACDIN.RM244.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM251.ZON:MODE
Point Name: ACDIN.RM251.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM253.ZON:MODE
Point Name: ACDIN.RM253.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM255.ZON:MODE
Point Name: ACDIN.RM255.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM256.ZON:MODE
Point Name: ACDIN.RM256.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM257.ZON:MODE
Point Name: ACDIN.RM257.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM258.ZON:MODE
Point Name: ACDIN.RM258.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM260.ZON:MODE
Point Name: ACDIN.RM260.LOUNGE:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM261.ZON:MODE
Point Name: ACDIN.RM261.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM262.ZON:MODE
Point Name: ACDIN.RM262.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM263.ZON:MODE
Point Name: ACDIN.RM263.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM301.ZON:MODE
Point Name: ACDIN.RM301.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM302.ZON:MODE
Point Name: ACDIN.RM302.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM303.ZON:MODE
Point Name: ACDIN.RM303.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM304.ZON:MODE
Point Name: ACDIN.RM304.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM305.ZON:MODE
Point Name: ACDIN.RM305.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM311.ZON:MODE
Point Name: ACDIN.RM311.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM312.ZON:MODE
Point Name: ACDIN.RM312.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM314.ZON:MODE
Point Name: ACDIN.RM314.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM315.ZON:MODE
Point Name: ACDIN.RM315.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM316.ZON:MODE
Point Name: ACDIN.RM316.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM317.ZON:MODE
Point Name: ACDIN.RM317.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM318.ZON:MODE
Point Name: ACDIN.RM318.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM319.ZON:MODE
Point Name: ACDIN.RM319.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM320.ZON:MODE
Point Name: ACDIN.RM320.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM321.ZON:MODE
Point Name: ACDIN.RM321.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM330.ZON:MODE
Point Name: ACDIN.RM330.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM331.ZON:MODE
Point Name: ACDIN.RM331.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM335.ZON:MODE
Point Name: ACDIN.RM335.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM340.ZON:MODE
Point Name: ACDIN.RM340.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM345.ZON:MODE
Point Name: ACDIN.RM345.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM351.ZON:MODE
Point Name: ACDIN.RM351.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM352.ZON:MODE
Point Name: ACDIN.RM352.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM353.ZON:MODE
Point Name: ACDIN.RM353.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM355.ZON:MODE
Point Name: ACDIN.RM355.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM356.ZON:MODE
Point Name: ACDIN.RM356.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM357.ZON:MODE
Point Name: ACDIN.RM357.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM358.ZON:MODE
Point Name: ACDIN.RM358.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM360.ZON:MODE
Point Name: ACDIN.RM360.LOUNGE:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM362.ZON:MODE
Point Name: ACDIN.RM362.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM363.ZON:MODE
Point Name: ACDIN.RM363.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM364.ZON:MODE
Point Name: ACDIN.RM364.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM365.ZON:MODE
Point Name: ACDIN.RM365.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM366.ZON:MODE
Point Name: ACDIN.RM366.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM368.ZON:MODE
Point Name: ACDIN.RM368.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM369.ZON:MODE
Point Name: ACDIN.RM369.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM370.ZON:MODE
Point Name: ACDIN.RM370.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.RM371.ZON:MODE
Point Name: ACDIN.RM371.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Point System Name: ACDIN.VAV022:DAY.NGT
Point Name: ACDIN.VAV022:DAY.NGT
Point Type: LDO
Descriptor: VAV022RM262
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 17 29
Inverted: No
Point System Name: ACDIN.VAV022.CTLFLMN
Point Name: ACDIN.VAV022.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 17 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV022.ORGSTPT
Point Name: ACDIN.VAV022.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV023:DAY.NGT
Point Name: ACDIN.VAV023:DAY.NGT
Point Type: LDO
Descriptor: VAV023RM261
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 16 29
Inverted: No
Point System Name: ACDIN.VAV023.CTLFLMN
Point Name: ACDIN.VAV023.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 16 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV023.ORGSTPT
Point Name: ACDIN.VAV023.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV024:DAY.NGT
Point Name: ACDIN.VAV024:DAY.NGT
Point Type: LDO
Descriptor: VAV024RM255
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 15 29
Inverted: No
Point System Name: ACDIN.VAV024.CTLFLMN
Point Name: ACDIN.VAV024.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 15 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV024.ORGSTPT
Point Name: ACDIN.VAV024.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV025:DAY.NGT
Point Name: ACDIN.VAV025:DAY.NGT
Point Type: LDO
Descriptor: VAV025RM258
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 13 29
Inverted: No
Point System Name: ACDIN.VAV025.CTLFLMN
Point Name: ACDIN.VAV025.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 13 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV025.ORGSTPT
Point Name: ACDIN.VAV025.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV026:DAY.NGT
Point Name: ACDIN.VAV026:DAY.NGT
Point Type: LDO
Descriptor: VAV026RM257
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 12 29
Inverted: No
Point System Name: ACDIN.VAV026.CTLFLMN
Point Name: ACDIN.VAV026.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 12 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV026.ORGSTPT
Point Name: ACDIN.VAV026.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV027:DAY.NGT
Point Name: ACDIN.VAV027:DAY.NGT
Point Type: LDO
Descriptor: VAV027RM243
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 10 29
Inverted: No
Point System Name: ACDIN.VAV027.CTLFLMN
Point Name: ACDIN.VAV027.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 476.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV027.ORGSTPT
Point Name: ACDIN.VAV027.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV028:DAY.NGT
Point Name: ACDIN.VAV028:DAY.NGT
Point Type: LDO
Descriptor: VAV028RM251
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 20 29
Inverted: No
Point System Name: ACDIN.VAV028.CTLFLMN
Point Name: ACDIN.VAV028.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 152.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 20 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV028.ORGSTPT
Point Name: ACDIN.VAV028.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV029:DAY.NGT
Point Name: ACDIN.VAV029:DAY.NGT
Point Type: LDO
Descriptor: VAV029RM201
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 06 29
Inverted: No
Point System Name: ACDIN.VAV029.CTLFLMN
Point Name: ACDIN.VAV029.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 124.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 06 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV029.ORGSTPT
Point Name: ACDIN.VAV029.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV030:DAY.NGT
Point Name: ACDIN.VAV030:DAY.NGT
Point Type: LDO
Descriptor: VAV030RM263
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 18 29
Inverted: No
Point System Name: ACDIN.VAV030.CTLFLMN
Point Name: ACDIN.VAV030.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 18 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV030.ORGSTPT
Point Name: ACDIN.VAV030.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV031:DAY.NGT
Point Name: ACDIN.VAV031:DAY.NGT
Point Type: LDO
Descriptor: VAV031RM260
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 19 29
Inverted: No
Point System Name: ACDIN.VAV031.CTLFLMN
Point Name: ACDIN.VAV031.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 152.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 19 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV031.ORGSTPT
Point Name: ACDIN.VAV031.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV032:DAY.NGT
Point Name: ACDIN.VAV032:DAY.NGT
Point Type: LDO
Descriptor: VAVO32RM244
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 21 29
Inverted: No
Point System Name: ACDIN.VAV032.CTLFLMN
Point Name: ACDIN.VAV032.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 700.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 21 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV032.ORGSTPT
Point Name: ACDIN.VAV032.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV033:DAY.NGT
Point Name: ACDIN.VAV033:DAY.NGT
Point Type: LDO
Descriptor: VAV033RM240
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 08 29
Inverted: No
Point System Name: ACDIN.VAV033.CTLFLMN
Point Name: ACDIN.VAV033.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 08 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV033.ORGSTPT
Point Name: ACDIN.VAV033.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV034:DAY.NGT
Point Name: ACDIN.VAV034:DAY.NGT
Point Type: LDO
Descriptor: VAV034RM241
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 09 29
Inverted: No
Point System Name: ACDIN.VAV034.CTLFLMN
Point Name: ACDIN.VAV034.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 376.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 09 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV034.ORGSTPT
Point Name: ACDIN.VAV034.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV035:DAY.NGT
Point Name: ACDIN.VAV035:DAY.NGT
Point Type: LDO
Descriptor: VAV035RM223
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 07 29
Inverted: No
Point System Name: ACDIN.VAV035.CTLFLMN
Point Name: ACDIN.VAV035.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV035.ORGSTPT
Point Name: ACDIN.VAV035.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV036:DAY.NGT
Point Name: ACDIN.VAV036:DAY.NGT
Point Type: LDO
Descriptor: VAV036RM220
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 06 29
Inverted: No
Point System Name: ACDIN.VAV036.CTLFLMN
Point Name: ACDIN.VAV036.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 244.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 06 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV036.ORGSTPT
Point Name: ACDIN.VAV036.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV037:DAY.NGT
Point Name: ACDIN.VAV037:DAY.NGT
Point Type: LDO
Descriptor: VAV037RM222
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 04 29
Inverted: No
Point System Name: ACDIN.VAV037.CTLFLMN
Point Name: ACDIN.VAV037.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 04 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV037.ORGSTPT
Point Name: ACDIN.VAV037.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV038:DAY.NGT
Point Name: ACDIN.VAV038:DAY.NGT
Point Type: LDO
Descriptor: VAV038RM221
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 05 29
Inverted: No
Point System Name: ACDIN.VAV038.CTLFLMN
Point Name: ACDIN.VAV038.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV038.ORGSTPT
Point Name: ACDIN.VAV038.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV039:DAY.NGT
Point Name: ACDIN.VAV039:DAY.NGT
Point Type: LDO
Descriptor: VAV039RM210
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 30 29
Inverted: No
Point System Name: ACDIN.VAV039.CTLFLMN
Point Name: ACDIN.VAV039.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 300.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 30 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV039.ORGSTPT
Point Name: ACDIN.VAV039.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV041:DAY.NGT
Point Name: ACDIN.VAV041:DAY.NGT
Point Type: LDO
Descriptor: VAV041RM242
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 22 29
Inverted: No
Point System Name: ACDIN.VAV041.CTLFLMN
Point Name: ACDIN.VAV041.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 500.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 22 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV041.ORGSTPT
Point Name: ACDIN.VAV041.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV042:DAY.NGT
Point Name: ACDIN.VAV042:DAY.NGT
Point Type: LDO
Descriptor: VAV042RM234
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 23 29
Inverted: No
Point System Name: ACDIN.VAV042.CTLFLMN
Point Name: ACDIN.VAV042.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 23 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV042.ORGSTPT
Point Name: ACDIN.VAV042.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV043:DAY.NGT
Point Name: ACDIN.VAV043:DAY.NGT
Point Type: LDO
Descriptor: VAV043RM231
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 24 29
Inverted: No
Point System Name: ACDIN.VAV043.CTLFLMN
Point Name: ACDIN.VAV043.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 272.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 24 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV043.ORGSTPT
Point Name: ACDIN.VAV043.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV044:DAY.NGT
Point Name: ACDIN.VAV044:DAY.NGT
Point Type: LDO
Descriptor: VAV044RM236
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 05 29
Inverted: No
Point System Name: ACDIN.VAV044.CTLFLMN
Point Name: ACDIN.VAV044.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV044.ORGSTPT
Point Name: ACDIN.VAV044.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV045:DAY.NGT
Point Name: ACDIN.VAV045:DAY.NGT
Point Type: LDO
Descriptor: VAV045RM202
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 04 29
Inverted: No
Point System Name: ACDIN.VAV045.CTLFLMN
Point Name: ACDIN.VAV045.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 284.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 04 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV045.ORGSTPT
Point Name: ACDIN.VAV045.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV046:DAY.NGT
Point Name: ACDIN.VAV046:DAY.NGT
Point Type: LDO
Descriptor: VAV046RM203
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 03 29
Inverted: No
Point System Name: ACDIN.VAV046.CTLFLMN
Point Name: ACDIN.VAV046.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 03 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV046.ORGSTPT
Point Name: ACDIN.VAV046.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV047:DAY.NGT
Point Name: ACDIN.VAV047:DAY.NGT
Point Type: LDO
Descriptor: VAV047RM205
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 01 29
Inverted: No
Point System Name: ACDIN.VAV047.CTLFLMN
Point Name: ACDIN.VAV047.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 232.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV047.ORGSTPT
Point Name: ACDIN.VAV047.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV048:DAY.NGT
Point Name: ACDIN.VAV048:DAY.NGT
Point Type: LDO
Descriptor: VAV048RMRM201
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 07 29
Inverted: No
Point System Name: ACDIN.VAV048.CTLFLMN
Point Name: ACDIN.VAV048.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV048.ORGSTPT
Point Name: ACDIN.VAV048.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV049:DAY.NGT
Point Name: ACDIN.VAV049:DAY.NGT
Point Type: LDO
Descriptor: VAV049RM211
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 26 29
Inverted: No
Point System Name: ACDIN.VAV049.CTLFLMN
Point Name: ACDIN.VAV049.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 26 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV049.ORGSTPT
Point Name: ACDIN.VAV049.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV050:DAY.NGT
Point Name: ACDIN.VAV050:DAY.NGT
Point Type: LDO
Descriptor: VAV050RM212
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 27 29
Inverted: No
Point System Name: ACDIN.VAV050.CTLFLMN
Point Name: ACDIN.VAV050.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 27 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV050.ORGSTPT
Point Name: ACDIN.VAV050.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV051:DAY.NGT
Point Name: ACDIN.VAV051:DAY.NGT
Point Type: LDO
Descriptor: VAV051RM213
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 28 29
Inverted: No
Point System Name: ACDIN.VAV051.CTLFLMN
Point Name: ACDIN.VAV051.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 28 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV051.ORGSTPT
Point Name: ACDIN.VAV051.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV052:DAY.NGT
Point Name: ACDIN.VAV052:DAY.NGT
Point Type: LDO
Descriptor: VAV052RM214
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 29 29
Inverted: No
Point System Name: ACDIN.VAV052.CTLFLMN
Point Name: ACDIN.VAV052.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 29 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV052.ORGSTPT
Point Name: ACDIN.VAV052.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV053:DAY.NGT
Point Name: ACDIN.VAV053:DAY.NGT
Point Type: LDO
Descriptor: VAV053RM215
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 01 29
Inverted: No
Point System Name: ACDIN.VAV053.CTLFLMN
Point Name: ACDIN.VAV053.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV053.ORGSTPT
Point Name: ACDIN.VAV053.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV054:DAY.NGT
Point Name: ACDIN.VAV054:DAY.NGT
Point Type: LDO
Descriptor: VAV054RM216
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 02 29
Inverted: No
Point System Name: ACDIN.VAV054.CTLFLMN
Point Name: ACDIN.VAV054.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 02 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV054.ORGSTPT
Point Name: ACDIN.VAV054.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV055:DAY.NGT
Point Name: ACDIN.VAV055:DAY.NGT
Point Type: LDO
Descriptor: VAV055 RM370
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 14 29
Inverted: No
Point System Name: ACDIN.VAV055.CTLFLMN
Point Name: ACDIN.VAV055.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 112.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 14 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV055.ORGSTPT
Point Name: ACDIN.VAV055.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV056:DAY.NGT
Point Name: ACDIN.VAV056:DAY.NGT
Point Type: LDO
Descriptor: VAV056RM369
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 13 29
Inverted: No
Point System Name: ACDIN.VAV056.CTLFLMN
Point Name: ACDIN.VAV056.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 13 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV056.ORGSTPT
Point Name: ACDIN.VAV056.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV057:DAY.NGT
Point Name: ACDIN.VAV057:DAY.NGT
Point Type: LDO
Descriptor: VAV057RM364
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 11 29
Inverted: No
Point System Name: ACDIN.VAV057.CTLFLMN
Point Name: ACDIN.VAV057.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 11 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV057.ORGSTPT
Point Name: ACDIN.VAV057.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV058:DAY.NGT
Point Name: ACDIN.VAV058:DAY.NGT
Point Type: LDO
Descriptor: VAV058RM363
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 12 29
Inverted: No
Point System Name: ACDIN.VAV058.CTLFLMN
Point Name: ACDIN.VAV058.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 12 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV058.ORGSTPT
Point Name: ACDIN.VAV058.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV059:DAY.NGT
Point Name: ACDIN.VAV059:DAY.NGT
Point Type: LDO
Descriptor: VAV059RM365
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 10 29
Inverted: No
Point System Name: ACDIN.VAV059.CTLFLMN
Point Name: ACDIN.VAV059.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 120.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV059.ORGSTPT
Point Name: ACDIN.VAV059.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV060:DAY.NGT
Point Name: ACDIN.VAV060:DAY.NGT
Point Type: LDO
Descriptor: VAV060RM366
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 09 29
Inverted: No
Point System Name: ACDIN.VAV060.CTLFLMN
Point Name: ACDIN.VAV060.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 09 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV060.ORGSTPT
Point Name: ACDIN.VAV060.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV061:DAY.NGT
Point Name: ACDIN.VAV061:DAY.NGT
Point Type: LDO
Descriptor: VAV061RM360
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 07 29
Inverted: No
Point System Name: ACDIN.VAV061.CTLFLMN
Point Name: ACDIN.VAV061.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 272.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV061.ORGSTPT
Point Name: ACDIN.VAV061.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV062:DAY.NGT
Point Name: ACDIN.VAV062:DAY.NGT
Point Type: LDO
Descriptor: VAV062RM371
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 15 29
Inverted: No
Point System Name: ACDIN.VAV062.CTLFLMN
Point Name: ACDIN.VAV062.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 52.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 15 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV062.ORGSTPT
Point Name: ACDIN.VAV062.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV063:DAY.NGT
Point Name: ACDIN.VAV063:DAY.NGT
Point Type: LDO
Descriptor: VAV063RM368
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 16 29
Inverted: No
Point System Name: ACDIN.VAV063.CTLFLMN
Point Name: ACDIN.VAV063.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 16 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV063.ORGSTPT
Point Name: ACDIN.VAV063.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV064:DAY.NGT
Point Name: ACDIN.VAV064:DAY.NGT
Point Type: LDO
Descriptor: VAV064RM362
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 08 29
Inverted: No
Point System Name: ACDIN.VAV064.CTLFLMN
Point Name: ACDIN.VAV064.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 08 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV064.ORGSTPT
Point Name: ACDIN.VAV064.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV065:DAY.NGT
Point Name: ACDIN.VAV065:DAY.NGT
Point Type: LDO
Descriptor: VAV065RM351
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 06 29
Inverted: No
Point System Name: ACDIN.VAV065.CTLFLMN
Point Name: ACDIN.VAV065.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 06 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV065.ORGSTPT
Point Name: ACDIN.VAV065.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV066:DAY.NGT
Point Name: ACDIN.VAV066:DAY.NGT
Point Type: LDO
Descriptor: VAV066RM352
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 05 29
Inverted: No
Point System Name: ACDIN.VAV066.CTLFLMN
Point Name: ACDIN.VAV066.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV066.ORGSTPT
Point Name: ACDIN.VAV066.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV067:DAY.NGT
Point Name: ACDIN.VAV067:DAY.NGT
Point Type: LDO
Descriptor: VAV067RM353
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 04 29
Inverted: No
Point System Name: ACDIN.VAV067.CTLFLMN
Point Name: ACDIN.VAV067.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 04 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV067.ORGSTPT
Point Name: ACDIN.VAV067.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV069:DAY.NGT
Point Name: ACDIN.VAV069:DAY.NGT
Point Type: LDO
Descriptor: VAV069RM355
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 18 29
Inverted: No
Point System Name: ACDIN.VAV069.CTLFLMN
Point Name: ACDIN.VAV069.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 18 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV069.ORGSTPT
Point Name: ACDIN.VAV069.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV070:DAY.NGT
Point Name: ACDIN.VAV070:DAY.NGT
Point Type: LDO
Descriptor: VAV070RM356
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 17 29
Inverted: No
Point System Name: ACDIN.VAV070.CTLFLMN
Point Name: ACDIN.VAV070.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 17 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV070.ORGSTPT
Point Name: ACDIN.VAV070.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV071:DAY.NGT
Point Name: ACDIN.VAV071:DAY.NGT
Point Type: LDO
Descriptor: VAV071RM357
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 20 29
Inverted: No
Point System Name: ACDIN.VAV071.CTLFLMN
Point Name: ACDIN.VAV071.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 20 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV071.ORGSTPT
Point Name: ACDIN.VAV071.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV072:DAY.NGT
Point Name: ACDIN.VAV072:DAY.NGT
Point Type: LDO
Descriptor: VAV072RM346
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 19 29
Inverted: No
Point System Name: ACDIN.VAV072.CTLFLMN
Point Name: ACDIN.VAV072.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 19 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV072.ORGSTPT
Point Name: ACDIN.VAV072.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV074:DAY.NGT
Point Name: ACDIN.VAV074:DAY.NGT
Point Type: LDO
Descriptor: VAV074RM358
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 21 29
Inverted: No
Point System Name: ACDIN.VAV074.CTLFLMN
Point Name: ACDIN.VAV074.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 21 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV074.ORGSTPT
Point Name: ACDIN.VAV074.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV075:DAY.NGT
Point Name: ACDIN.VAV075:DAY.NGT
Point Type: LDO
Descriptor: VAV075RM341
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 23 29
Inverted: No
Point System Name: ACDIN.VAV075.CTLFLMN
Point Name: ACDIN.VAV075.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 352.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 23 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV075.ORGSTPT
Point Name: ACDIN.VAV075.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV076:DAY.NGT
Point Name: ACDIN.VAV076:DAY.NGT
Point Type: LDO
Descriptor: VAV076RM345
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 03 29
Inverted: No
Point System Name: ACDIN.VAV076.CTLFLMN
Point Name: ACDIN.VAV076.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 352.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 03 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV076.ORGSTPT
Point Name: ACDIN.VAV076.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV077:DAY.NGT
Point Name: ACDIN.VAV077:DAY.NGT
Point Type: LDO
Descriptor: VAV077RM331
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 22 29
Inverted: No
Point System Name: ACDIN.VAV077.CTLFLMN
Point Name: ACDIN.VAV077.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 108.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 22 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV077.ORGSTPT
Point Name: ACDIN.VAV077.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV078:DAY.NGT
Point Name: ACDIN.VAV078:DAY.NGT
Point Type: LDO
Descriptor: VAV078RM335
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 02 29
Inverted: No
Point System Name: ACDIN.VAV078.CTLFLMN
Point Name: ACDIN.VAV078.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 352.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 02 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV078.ORGSTPT
Point Name: ACDIN.VAV078.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV079:DAY.NGT
Point Name: ACDIN.VAV079:DAY.NGT
Point Type: LDO
Descriptor: VAV079RM330
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 01 29
Inverted: No
Point System Name: ACDIN.VAV079.CTLFLMN
Point Name: ACDIN.VAV079.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 352.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 3 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV079.ORGSTPT
Point Name: ACDIN.VAV079.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV080:DAY.NGT
Point Name: ACDIN.VAV080:DAY.NGT
Point Type: LDO
Descriptor: VAV080RM301
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 19 29
Inverted: No
Point System Name: ACDIN.VAV080.CTLFLMN
Point Name: ACDIN.VAV080.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 416.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 19 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV080.HEAT COOL
Point Name: ACDIN.VAV080.HEAT COOL
Point Type: LDI
Descriptor: HEAT COOL SWITCH
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 19 05
Normally Closed: No
Point System Name: ACDIN.VAV080.HTG LOOPOUT
Point Name: ACDIN.VAV080.HTG LOOPOUT
Point Type: LAI
Descriptor: HEATING LOOP
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 19 80
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV080.ORGSTPT
Point Name: ACDIN.VAV080.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV081:DAY.NGT
Point Name: ACDIN.VAV081:DAY.NGT
Point Type: LDO
Descriptor: VAV081RM302
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 20 29
Inverted: No
Point System Name: ACDIN.VAV081.CTLFLMN
Point Name: ACDIN.VAV081.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 460.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 20 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV081.HEAT COOL
Point Name: ACDIN.VAV081.HEAT COOL
Point Type: LDI
Descriptor: HEAT COOL SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 20 05
Normally Closed: No
Point System Name: ACDIN.VAV081.HTG LOOPOUT
Point Name: ACDIN.VAV081.HTG LOOPOUT
Point Type: LAI
Descriptor: HEATING LOOP
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 20 80
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 0.4
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV081.ORGSTPT
Point Name: ACDIN.VAV081.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV082:DAY.NGT
Point Name: ACDIN.VAV082:DAY.NGT
Point Type: LDO
Descriptor: VAV082RM303
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 22 29
Inverted: No
Point System Name: ACDIN.VAV082.CTLFLMN
Point Name: ACDIN.VAV082.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 22 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV082.ORGSTPT
Point Name: ACDIN.VAV082.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV083:DAY.NGT
Point Name: ACDIN.VAV083:DAY.NGT
Point Type: LDO
Descriptor: VAV083RM304
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 23 29
Inverted: No
Point System Name: ACDIN.VAV083.CTLFLMN
Point Name: ACDIN.VAV083.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 23 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV083.ORGSTPT
Point Name: ACDIN.VAV083.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 77.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV084:DAY.NGT
Point Name: ACDIN.VAV084:DAY.NGT
Point Type: LDO
Descriptor: VAV084RM305
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 24 29
Inverted: No
Point System Name: ACDIN.VAV084.CTLFLMN
Point Name: ACDIN.VAV084.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 24 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV084.ORGSTPT
Point Name: ACDIN.VAV084.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 78.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV085:DAY.NGT
Point Name: ACDIN.VAV085:DAY.NGT
Point Type: LDO
Descriptor: VAV085RM311
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 17 29
Inverted: No
Point System Name: ACDIN.VAV085.CTLFLMN
Point Name: ACDIN.VAV085.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 17 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV085.ORGSTPT
Point Name: ACDIN.VAV085.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV086:DAY.NGT
Point Name: ACDIN.VAV086:DAY.NGT
Point Type: LDO
Descriptor: VAV086RM312
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 16 29
Inverted: No
Point System Name: ACDIN.VAV086.CTLFLMN
Point Name: ACDIN.VAV086.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 16 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV086.ORGSTPT
Point Name: ACDIN.VAV086.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV087:DAY.NGT
Point Name: ACDIN.VAV087:DAY.NGT
Point Type: LDO
Descriptor: VAV087RM314
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 15 29
Inverted: No
Point System Name: ACDIN.VAV087.CTLFLMN
Point Name: ACDIN.VAV087.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 15 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV087.ORGSTPT
Point Name: ACDIN.VAV087.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 73.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV088:DAY.NGT
Point Name: ACDIN.VAV088:DAY.NGT
Point Type: LDO
Descriptor: VAV088RM315
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 14 29
Inverted: No
Point System Name: ACDIN.VAV088.CTLFLMN
Point Name: ACDIN.VAV088.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 14 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV088.ORGSTPT
Point Name: ACDIN.VAV088.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV089:DAY.NGT
Point Name: ACDIN.VAV089:DAY.NGT
Point Type: LDO
Descriptor: VAV089RM319
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 08 29
Inverted: No
Point System Name: ACDIN.VAV089.CTLFLMN
Point Name: ACDIN.VAV089.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 216.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 08 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV089.ORGSTPT
Point Name: ACDIN.VAV089.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV090:DAY.NGT
Point Name: ACDIN.VAV090:DAY.NGT
Point Type: LDO
Descriptor: VAV090RM321
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 09 29
Inverted: No
Point System Name: ACDIN.VAV090.CTLFLMN
Point Name: ACDIN.VAV090.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 09 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV090.ORGSTPT
Point Name: ACDIN.VAV090.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV091:DAY.NGT
Point Name: ACDIN.VAV091:DAY.NGT
Point Type: LDO
Descriptor: VAV091RM320
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 10 29
Inverted: No
Point System Name: ACDIN.VAV091.CTLFLMN
Point Name: ACDIN.VAV091.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV091.ORGSTPT
Point Name: ACDIN.VAV091.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV092:DAY.NGT
Point Name: ACDIN.VAV092:DAY.NGT
Point Type: LDO
Descriptor: VAV092RM318
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 11 29
Inverted: No
Point System Name: ACDIN.VAV092.CTLFLMN
Point Name: ACDIN.VAV092.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 11 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV092.ORGSTPT
Point Name: ACDIN.VAV092.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV093:DAY.NGT
Point Name: ACDIN.VAV093:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 13 29
Inverted: No
Point System Name: ACDIN.VAV093.CTLFLMN
Point Name: ACDIN.VAV093.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 12 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV093.ORGSTPT
Point Name: ACDIN.VAV093.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV094:DAY.NGT
Point Name: ACDIN.VAV094:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 12 29
Inverted: No
Point System Name: ACDIN.VAV094.CTLFLMN
Point Name: ACDIN.VAV094.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 13 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV094.ORGSTPT
Point Name: ACDIN.VAV094.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV095:DAY.NGT
Point Name: ACDIN.VAV095:DAY.NGT
Point Type: LDO
Descriptor: VAV095RM256
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 14 29
Inverted: No
Point System Name: ACDIN.VAV095.CTLFLMN
Point Name: ACDIN.VAV095.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 14 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV095.ORGSTPT
Point Name: ACDIN.VAV095.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV096:DAY.NGT
Point Name: ACDIN.VAV096:DAY.NGT
Point Type: LDO
Descriptor: VAV096RM253
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 11 29
Inverted: No
Point System Name: ACDIN.VAV096.CTLFLMN
Point Name: ACDIN.VAV096.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 11 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV096.ORGSTPT
Point Name: ACDIN.VAV096.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV097:DAY.NGT
Point Name: ACDIN.VAV097:DAY.NGT
Point Type: LDO
Descriptor: VAV097RM217
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 03 29
Inverted: No
Point System Name: ACDIN.VAV097.CTLFLMN
Point Name: ACDIN.VAV097.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 24.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 2 03 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV097.ORGSTPT
Point Name: ACDIN.VAV097.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.VAV098:DAY.NGT
Point Name: ACDIN.VAV098:DAY.NGT
Point Type: LDO
Descriptor: VAV098RM204
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 02 29
Inverted: No
Point System Name: ACDIN.VAV098.CTLFLMN
Point Name: ACDIN.VAV098.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: 1 02 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: ACDIN.VAV098.ORGSTPT
Point Name: ACDIN.VAV098.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: ACDIN.PXCM44
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.COND
Point Name: ACDIN.COND
Point Type: LPACI
Descriptor: CONDENSATE MTR
Value: 659090.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: NOURSE.PXCM34
Point Address: 0 05 05
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
Point System Name: ACDIN.CONM
Point Name: ACDIN.CONM
Point Type: LPACI
Descriptor: CONDENSATE MTR
Value: 148610.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: NOURSE.PXCM34
Point Address: 0 05 05
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
BLN04 MYERS.PENTHOUSE: Supplied Field Panel number out of range
BLN04 MYERS.LOWERLEVEL: Supplied Field Panel number out of range
BACDev_205003: 3rd party BACnet panels cannot resolve wildcards
BACDev_204003: 3rd party BACnet panels cannot resolve wildcards
Point System Name: ACDIN.EF02.EF04.PGM:PPCL Address
Point Name: ACDIN.EF02.EF04.PGM:PPCL Address
Object Name: ACDIN.EF02.EF04.PGM:PPCL Address
Object ID: analog-value - 10300
Point Type: LAI
Descriptor:
Value: 0
BACnet Command Priority Array
None
Relinquish Default: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: ACDIN.EF02.FAN.STATUS
Point Name: ACDIN.EF02.FAN.STATUS
Object Name: ACDIN.EF02.FAN.STATUS
Object ID: binary-value - 10
Point Type: LDO
Descriptor: EF02 STATUS
Value: ON
BACnet Command Priority Array
16 - ON
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF02.VFD.CURRENT
Point Name: ACDIN.EF02.VFD.CURRENT
Object Name: ACDIN.EF02.VFD.CURRENT
Object ID: analog-value - 17
Point Type: LAO
Descriptor: AF02 CURRENT
Value: 2.8
BACnet Command Priority Array
16 - 2.8
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: A
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF02.VFD.MAX.SPEED
Point Name: ACDIN.EF02.VFD.MAX.SPEED
Object Name: ACDIN.EF02.VFD.MAX.SPEED
Object ID: analog-value - 14
Point Type: LAO
Descriptor: EF02 MAX SPD
Value: 60.0
BACnet Command Priority Array
16 - 60.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF02.VFD.POWER
Point Name: ACDIN.EF02.VFD.POWER
Object Name: ACDIN.EF02.VFD.POWER
Object ID: analog-value - 18
Point Type: LAO
Descriptor: EF02 POWER
Value: 11264.0
BACnet Command Priority Array
16 - 11264.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: kW h
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF02.VFD.SPEED.ACT
Point Name: ACDIN.EF02.VFD.SPEED.ACT
Object Name: ACDIN.EF02.VFD.SPEED.ACT
Object ID: analog-value - 16
Point Type: LAO
Descriptor: EF02 SPD ACT
Value: 30.0
BACnet Command Priority Array
16 - 30.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF02.VFD.SPEED.CMD
Point Name: ACDIN.EF02.VFD.SPEED.CMD
Object Name: ACDIN.EF02.VFD.SPEED.CMD
Object ID: analog-value - 15
Point Type: LAO
Descriptor: EF02 SPD CMD
Value: 30.0
BACnet Command Priority Array
16 - 30.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF02.VFDFAULT
Point Name: ACDIN.EF02.VFDFAULT
Object Name: ACDIN.EF02.VFDFAULT
Object ID: binary-value - 11
Point Type: LDO
Descriptor: EF02 VFD FAULT
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF02.VFDFAULT.CLEAR
Point Name: ACDIN.EF02.VFDFAULT.CLEAR
Object Name: ACDIN.EF02.VFDFAULT.CLEAR
Object ID: binary-value - 12
Point Type: LDO
Descriptor: EFO2 FLT CLEAR
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF03.EF12.PGM:PPCL Address
Point Name: ACDIN.EF03.EF12.PGM:PPCL Address
Object Name: ACDIN.EF03.EF12.PGM:PPCL Address
Object ID: analog-value - 10100
Point Type: LAI
Descriptor:
Value: 0
BACnet Command Priority Array
None
Relinquish Default: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: ACDIN.EF03.FAN.STATUS
Point Name: ACDIN.EF03.FAN.STATUS
Object Name: ACDIN.EF03.FAN.STATUS
Object ID: binary-value - 0
Point Type: LDO
Descriptor: EF03 STATUS
Value: ON
BACnet Command Priority Array
16 - ON
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF03.VFD.CURRENT
Point Name: ACDIN.EF03.VFD.CURRENT
Object Name: ACDIN.EF03.VFD.CURRENT
Object ID: analog-value - 4
Point Type: LAO
Descriptor: EF03 CURRENT
Value: 1.9
BACnet Command Priority Array
16 - 1.9
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: A
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF03.VFD.MAX.SPEED
Point Name: ACDIN.EF03.VFD.MAX.SPEED
Object Name: ACDIN.EF03.VFD.MAX.SPEED
Object ID: analog-value - 1
Point Type: LAO
Descriptor: EF03 MAX SPD
Value: 60.0
BACnet Command Priority Array
16 - 60.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF03.VFD.POWER
Point Name: ACDIN.EF03.VFD.POWER
Object Name: ACDIN.EF03.VFD.POWER
Object ID: analog-value - 5
Point Type: LAO
Descriptor: EF03 POWER
Value: 1966.0
BACnet Command Priority Array
16 - 1966.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: kW h
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF03.VFD.SPEED.ACT
Point Name: ACDIN.EF03.VFD.SPEED.ACT
Object Name: ACDIN.EF03.VFD.SPEED.ACT
Object ID: analog-value - 3
Point Type: LAO
Descriptor: EF03 SPD ACT
Value: 30.0
BACnet Command Priority Array
16 - 30.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF03.VFD.SPEED.CMD
Point Name: ACDIN.EF03.VFD.SPEED.CMD
Object Name: ACDIN.EF03.VFD.SPEED.CMD
Object ID: analog-value - 2
Point Type: LAO
Descriptor: EF03 SPD CMD
Value: 30.0
BACnet Command Priority Array
16 - 30.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF03.VFDFAULT
Point Name: ACDIN.EF03.VFDFAULT
Object Name: ACDIN.EF03.VFDFAULT
Object ID: binary-value - 1
Point Type: LDO
Descriptor: EF03 VFD FAULT
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF03.VFDFAULT.CLEAR
Point Name: ACDIN.EF03.VFDFAULT.CLEAR
Object Name: ACDIN.EF03.VFDFAULT.CLEAR
Object ID: binary-value - 2
Point Type: LDO
Descriptor: EF03 FLT CLEAR
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF04.FAN.STATUS
Point Name: ACDIN.EF04.FAN.STATUS
Object Name: ACDIN.EF04.FAN.STATUS
Object ID: binary-value - 13
Point Type: LDO
Descriptor: EF04 STATUS
Value: ON
BACnet Command Priority Array
16 - ON
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF04.VFD.CURRENT
Point Name: ACDIN.EF04.VFD.CURRENT
Object Name: ACDIN.EF04.VFD.CURRENT
Object ID: analog-value - 22
Point Type: LAO
Descriptor: EF04 CURRENT
Value: 3.8
BACnet Command Priority Array
16 - 3.8
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: A
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF04.VFD.MAX.SPEED
Point Name: ACDIN.EF04.VFD.MAX.SPEED
Object Name: ACDIN.EF04.VFD.MAX.SPEED
Object ID: analog-value - 19
Point Type: LAO
Descriptor: EF04 MAX SPD
Value: 60.0
BACnet Command Priority Array
16 - 60.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF04.VFD.POWER
Point Name: ACDIN.EF04.VFD.POWER
Object Name: ACDIN.EF04.VFD.POWER
Object ID: analog-value - 23
Point Type: LAO
Descriptor: EF04 POWER
Value: 4024.0
BACnet Command Priority Array
16 - 4024.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: kW h
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF04.VFD.SPEED.ACT
Point Name: ACDIN.EF04.VFD.SPEED.ACT
Object Name: ACDIN.EF04.VFD.SPEED.ACT
Object ID: analog-value - 21
Point Type: LAO
Descriptor: EF04 SPD ACT
Value: 88.33
BACnet Command Priority Array
16 - 88.33
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF04.VFD.SPEED.CMD
Point Name: ACDIN.EF04.VFD.SPEED.CMD
Object Name: ACDIN.EF04.VFD.SPEED.CMD
Object ID: analog-value - 20
Point Type: LAO
Descriptor: EF04 SPD CMD
Value: 90.0
BACnet Command Priority Array
16 - 90.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF04.VFDFAULT
Point Name: ACDIN.EF04.VFDFAULT
Object Name: ACDIN.EF04.VFDFAULT
Object ID: binary-value - 14
Point Type: LDO
Descriptor: EF04 VFD FAULT
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF04.VFDFAULT.CLEAR
Point Name: ACDIN.EF04.VFDFAULT.CLEAR
Object Name: ACDIN.EF04.VFDFAULT.CLEAR
Object ID: binary-value - 15
Point Type: LDO
Descriptor: EF04 FLT CLEAR
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF12.FAN.STATUS
Point Name: ACDIN.EF12.FAN.STATUS
Object Name: ACDIN.EF12.FAN.STATUS
Object ID: binary-value - 3
Point Type: LDO
Descriptor: EF12 STATUS
Value: ON
BACnet Command Priority Array
16 - ON
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF12.VFD.CURRENT
Point Name: ACDIN.EF12.VFD.CURRENT
Object Name: ACDIN.EF12.VFD.CURRENT
Object ID: analog-value - 9
Point Type: LAO
Descriptor: EF12 CURRENT
Value: 4.9
BACnet Command Priority Array
16 - 4.9
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: A
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF12.VFD.MAX.SPEED
Point Name: ACDIN.EF12.VFD.MAX.SPEED
Object Name: ACDIN.EF12.VFD.MAX.SPEED
Object ID: analog-value - 6
Point Type: LAO
Descriptor: EF12 MAX SPD
Value: 60.0
BACnet Command Priority Array
16 - 60.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF12.VFD.POWER
Point Name: ACDIN.EF12.VFD.POWER
Object Name: ACDIN.EF12.VFD.POWER
Object ID: analog-value - 10
Point Type: LAO
Descriptor: EF12 POWER
Value: 7626.0
BACnet Command Priority Array
16 - 7626.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: kW h
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF12.VFD.SPEED.ACT
Point Name: ACDIN.EF12.VFD.SPEED.ACT
Object Name: ACDIN.EF12.VFD.SPEED.ACT
Object ID: analog-value - 8
Point Type: LAO
Descriptor: EF12 SPD ACT
Value: 56.67
BACnet Command Priority Array
16 - 56.67
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF12.VFD.SPEED.CMD
Point Name: ACDIN.EF12.VFD.SPEED.CMD
Object Name: ACDIN.EF12.VFD.SPEED.CMD
Object ID: analog-value - 7
Point Type: LAO
Descriptor: EF12 SPD CMD
Value: 55.0
BACnet Command Priority Array
16 - 55.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.EF12.VFDFAULT
Point Name: ACDIN.EF12.VFDFAULT
Object Name: ACDIN.EF12.VFDFAULT
Object ID: binary-value - 4
Point Type: LDO
Descriptor: EF12 VFD FAULT
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.EF12.VFDFAULT.CLEAR
Point Name: ACDIN.EF12.VFDFAULT.CLEAR
Object Name: ACDIN.EF12.VFDFAULT.CLEAR
Object ID: binary-value - 5
Point Type: LDO
Descriptor: EF12 FLT CLEAR
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD1.OPTIC
Point Name: ACDIN.HOOD1.OPTIC
Object Name: ACDIN.HOOD1.OPTIC
Object ID: binary-value - 19
Point Type: LDO
Descriptor: HOOD1 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD1.TEMP
Point Name: ACDIN.HOOD1.TEMP
Object Name: ACDIN.HOOD1.TEMP
Object ID: analog-value - 27
Point Type: LAO
Descriptor: HOOD1 TEMP
Value: 72.0
BACnet Command Priority Array
16 - 72.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD2.OPTIC
Point Name: ACDIN.HOOD2.OPTIC
Object Name: ACDIN.HOOD2.OPTIC
Object ID: binary-value - 16
Point Type: LDO
Descriptor: HOOD2 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD2.TEMP
Point Name: ACDIN.HOOD2.TEMP
Object Name: ACDIN.HOOD2.TEMP
Object ID: analog-value - 24
Point Type: LAO
Descriptor: HOOD2 TEMP
Value: 74.0
BACnet Command Priority Array
16 - 74.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD3.OPTIC
Point Name: ACDIN.HOOD3.OPTIC
Object Name: ACDIN.HOOD3.OPTIC
Object ID: binary-value - 17
Point Type: LDO
Descriptor: HOOD3 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD3.TEMP
Point Name: ACDIN.HOOD3.TEMP
Object Name: ACDIN.HOOD3.TEMP
Object ID: analog-value - 25
Point Type: LAO
Descriptor: HOOD3 TEMP
Value: 73.0
BACnet Command Priority Array
16 - 73.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD4.OPTIC
Point Name: ACDIN.HOOD4.OPTIC
Object Name: ACDIN.HOOD4.OPTIC
Object ID: binary-value - 18
Point Type: LDO
Descriptor: HOOD4 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD4.TEMP
Point Name: ACDIN.HOOD4.TEMP
Object Name: ACDIN.HOOD4.TEMP
Object ID: analog-value - 26
Point Type: LAO
Descriptor: HOOD4 TEMP
Value: 69.0
BACnet Command Priority Array
16 - 69.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD5.OPTIC
Point Name: ACDIN.HOOD5.OPTIC
Object Name: ACDIN.HOOD5.OPTIC
Object ID: binary-value - 8
Point Type: LDO
Descriptor: HOOD5 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD5.TEMP
Point Name: ACDIN.HOOD5.TEMP
Object Name: ACDIN.HOOD5.TEMP
Object ID: analog-value - 12
Point Type: LAO
Descriptor: HOOD5 TEMP
Value: 72.0
BACnet Command Priority Array
16 - 72.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD6.OPTIC
Point Name: ACDIN.HOOD6.OPTIC
Object Name: ACDIN.HOOD6.OPTIC
Object ID: binary-value - 9
Point Type: LDO
Descriptor: HOOD6 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD6.TEMP
Point Name: ACDIN.HOOD6.TEMP
Object Name: ACDIN.HOOD6.TEMP
Object ID: analog-value - 13
Point Type: LAO
Descriptor: HOOD6 TEMP
Value: 73.0
BACnet Command Priority Array
16 - 73.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD7.OPTIC
Point Name: ACDIN.HOOD7.OPTIC
Object Name: ACDIN.HOOD7.OPTIC
Object ID: binary-value - 20
Point Type: LDO
Descriptor: HOOD7 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD7.TEMP
Point Name: ACDIN.HOOD7.TEMP
Object Name: ACDIN.HOOD7.TEMP
Object ID: analog-value - 28
Point Type: LAO
Descriptor: HOOD7 TEMP
Value: 95.0
BACnet Command Priority Array
16 - 95.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD8.OPTIC
Point Name: ACDIN.HOOD8.OPTIC
Object Name: ACDIN.HOOD8.OPTIC
Object ID: binary-value - 6
Point Type: LDO
Descriptor: HOOD8 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD8.TEMP
Point Name: ACDIN.HOOD8.TEMP
Object Name: ACDIN.HOOD8.TEMP
Object ID: analog-value - 11
Point Type: LAO
Descriptor: HOOD8 TEMP
Value: 72.0
BACnet Command Priority Array
16 - 72.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: ACDIN.HOOD9.OPTIC
Point Name: ACDIN.HOOD9.OPTIC
Object Name: ACDIN.HOOD9.OPTIC
Object ID: binary-value - 7
Point Type: LDO
Descriptor: HOOD9 OPTIC
Value: OFF
BACnet Command Priority Array
16 - OFF
Relinquish Default: OFF
Condition: -N-
Priority: BN16
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Point System Name: ACDIN.HOOD9.TEMP
Point Name: ACDIN.HOOD9.TEMP
Object Name: ACDIN.HOOD9.TEMP
Object ID: analog-value - 0
Point Type: LAO
Descriptor: HOOD 9 TEMP
Value: 76.0
BACnet Command Priority Array
16 - 76.0
Relinquish Default: 0.0
Condition: -N-
Priority: BN16
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7018
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
LDC_EF12: 3rd party BACnet panels cannot resolve wildcards
LDC_EF03: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD8: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD9: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD5: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD6: 3rd party BACnet panels cannot resolve wildcards
ACDIN.EF02: 3rd party BACnet panels cannot resolve wildcards
ACDIN.EF04: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD1: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD2: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD3: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD4: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD7: 3rd party BACnet panels cannot resolve wildcards
BLN3_41: Field Panel Not In Defined Field Panel List
BLN3_70: Field Panel Not In Defined Field Panel List
BLN3_4914: Field Panel Not In Defined Field Panel List
BLN3_7000: Field Panel Not In Defined Field Panel List
********************************************************************************
******************************** End of Report *********************************

## Rec Center
10/16/2017 Carleton College 02:58 PM
Panel Point Definition Report
Selection: RECCNTR.AH1.ALM, RECCNTR.AH1.CCV, RECCNTR.AH1.CO2, ...
(276 Points)
Point System Name: RECCNTR.AH1.ALM
Point Name: RECCNTR.AH1.ALM
Point Type: LDO
Descriptor: FAN RUN ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH1.CCV
Point Name: RECCNTR.AH1.CCV
Point Type: LAO
Descriptor: AH1 CLG.COIL VLV
Value: 0.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.CO2
Point Name: RECCNTR.AH1.CO2
Point Type: LAI
Descriptor: AH1 RA CO2 PPM
Value: 0.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 03
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.078125
Intercept: -280.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.DMN
Point Name: RECCNTR.AH1.DMN
Point Type: LAO
Descriptor: DAMPER MIN POS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.DMNSP
Point Name: RECCNTR.AH1.DMNSP
Point Type: LAO
Descriptor: DPR MIN POS STPT
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.ERR
Point Name: RECCNTR.AH1.ERR
Point Type: LAO
Descriptor: SPLY TMP ERROR
Value: 7.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.FLT
Point Name: RECCNTR.AH1.FLT
Point Type: LAI
Descriptor: AH1 FILTER DP
Value: 0.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000102
Intercept: -0.62512
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.FRZ
Point Name: RECCNTR.AH1.FRZ
Point Type: LDI
Descriptor: AH1 FREEZESTAT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 08 05
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH1.HCT
Point Name: RECCNTR.AH1.HCT
Point Type: LAI
Descriptor: AH1 HTG COIL TMP
Value: 64.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 120.0
Low Limit: 45.0
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.HCV
Point Name: RECCNTR.AH1.HCV
Point Type: LAO
Descriptor: AH1 HTG COIL VLV
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.LPO
Point Name: RECCNTR.AH1.LPO
Point Type: LAO
Descriptor: SUPPLY LOOP
Value: 49.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.MAC
Point Name: RECCNTR.AH1.MAC
Point Type: LAO
Descriptor: MIXED TEMP STPT
Value: 110.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.MAD
Point Name: RECCNTR.AH1.MAD
Point Type: LAO
Descriptor: AH1 MA DAMPERS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.MAT
Point Name: RECCNTR.AH1.MAT
Point Type: LAI
Descriptor: AH1 MA TEMP
Value: 64.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.OCC
Point Name: RECCNTR.AH1.OCC
Point Type: LDO
Descriptor: OCC UNOCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH1.OCC.RUN
Point Name: RECCNTR.AH1.OCC.RUN
Point Type: LDO
Descriptor: RUN IN OCC
Value: ON
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH1.OVRD
Point Name: RECCNTR.AH1.OVRD
Point Type: LDO
Descriptor: OVER RIDE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH1.PHC
Point Name: RECCNTR.AH1.PHC
Point Type: LAO
Descriptor: PREHEAT TMP STPT
Value: 53.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.PHT
Point Name: RECCNTR.AH1.PHT
Point Type: LAI
Descriptor: AH1 PHT COIL TMP
Value: 63.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 140.0
Low Limit: 42.0
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.PHV
Point Name: RECCNTR.AH1.PHV
Point Type: LAO
Descriptor: AH1 PHT COIL VLV
Value: 16.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.RAF
Point Name: RECCNTR.AH1.RAF
Point Type: L2SL
Descriptor: RELIEF FAN SS
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
On/Off Point Address: 2 04 24
Inverted: No
Proof Point Address: 2 04 23
Normally Closed: No
Proof Delay: 0 Informational Text
********************************************************************************
Point System Name: RECCNTR.AH1.RAH
Point Name: RECCNTR.AH1.RAH
Point Type: LAI
Descriptor: AH1 RA HUMID
Value: 109.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: % RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.003255
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.RAT
Point Name: RECCNTR.AH1.RAT
Point Type: LAI
Descriptor: AH1 RA TEMP
Value: 66.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 50.0
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.RFAN.EAD
Point Name: RECCNTR.AH1.RFAN.EAD
Point Type: L2SL
Descriptor: AH1 RFN EA DMPR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM38
On/Off Point Address: 0 07 01
Inverted: No
Proof Point Address: 0 09 01
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.AH1.RMS
Point Name: RECCNTR.AH1.RMS
Point Type: LAO
Descriptor: ROOM TEMP STPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.RMT
Point Name: RECCNTR.AH1.RMT
Point Type: LAI
Descriptor: AH1 ROOM TEMP
Value: 67.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 95.0
Low Limit: 50.0
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 01 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.RVF
Point Name: RECCNTR.AH1.RVF
Point Type: LAO
Descriptor: AH1 EX FN SPEED
Value: 0.0
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 04 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.SAC
Point Name: RECCNTR.AH1.SAC
Point Type: LAO
Descriptor: SPLY TEMP STPT
Value: 103.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH1.SAF
Point Name: RECCNTR.AH1.SAF
Point Type: LDO
Descriptor: SPLY START STOP
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 1 01 24
Inverted: No
********************************************************************************
Point System Name: RECCNTR.AH1.SAT
Point Name: RECCNTR.AH1.SAT
Point Type: LAI
Descriptor: AH1 SA TEMP
Value: 66.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 140.0
Low Limit: 42.0
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 02 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.SEA
Point Name: RECCNTR.AH1.SEA
Point Type: LDO
Descriptor: HT CL SEASON
Value: HEAT
Condition: -N-
Priority: NONE
Text Table: COOL_HEAT
0 - COOL
1 - HEAT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH1.SMKSAP
Point Name: RECCNTR.AH1.SMKSAP
Point Type: LDI
Descriptor: SMK/HI STATIC AL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 08 01
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.AH1.SPF
Point Name: RECCNTR.AH1.SPF
Point Type: LDI
Descriptor: FAN PROOF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 08 02
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH1.SVF
Point Name: RECCNTR.AH1.SVF
Point Type: LAO
Descriptor: AH1 SUPPLY SPEED
Value: 0.0
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 1 01 53
Actuator Type Voltage
Slope: 0.006104
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH1.WUP
Point Name: RECCNTR.AH1.WUP
Point Type: LDO
Descriptor: WARM UP MODE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH2.ALM
Point Name: RECCNTR.AH2.ALM
Point Type: LDO
Descriptor: FAN RUN ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH2.CCV
Point Name: RECCNTR.AH2.CCV
Point Type: LAO
Descriptor: AH2 CLG COIL VLV
Value: 9.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.CO2
Point Name: RECCNTR.AH2.CO2
Point Type: LAI
Descriptor: AH2 RA CO2 PPM
Value: 465.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 02 03
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.078125
Intercept: -280.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.DMN
Point Name: RECCNTR.AH2.DMN
Point Type: LAO
Descriptor: DAMPER MIN POS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.DMNSP
Point Name: RECCNTR.AH2.DMNSP
Point Type: LAO
Descriptor: DPR MIN POS STPT
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.ERR
Point Name: RECCNTR.AH2.ERR
Point Type: LAO
Descriptor: SPLY TMP ERROR
Value: 0.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.FLT
Point Name: RECCNTR.AH2.FLT
Point Type: LAI
Descriptor: AH2 FILTER DP
Value: 0.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 02 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000102
Intercept: -0.62512
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.FRZ
Point Name: RECCNTR.AH2.FRZ
Point Type: LDI
Descriptor: AH2 FREEZESTAT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 07 07
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH2.HCT
Point Name: RECCNTR.AH2.HCT
Point Type: LAI
Descriptor: AH2 HTG COIL TMP
Value: 65.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 02 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.HCV
Point Name: RECCNTR.AH2.HCV
Point Type: LAO
Descriptor: AH2 HTG COIL VLV
Value: 16.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.LPO
Point Name: RECCNTR.AH2.LPO
Point Type: LAO
Descriptor: SUPPLY LOOP
Value: 87.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.MAC
Point Name: RECCNTR.AH2.MAC
Point Type: LAO
Descriptor: MIXED TEMP STPT
Value: 57.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.MAD
Point Name: RECCNTR.AH2.MAD
Point Type: LAO
Descriptor: AH2 MA DAMPERS
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.MAT
Point Name: RECCNTR.AH2.MAT
Point Type: LAI
Descriptor: AH2 MA TEMP
Value: 64.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 45.0
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 02 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.OCC
Point Name: RECCNTR.AH2.OCC
Point Type: LDO
Descriptor: OCC UNOCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH2.OCC.RUN
Point Name: RECCNTR.AH2.OCC.RUN
Point Type: LDO
Descriptor: RUN IN OCC
Value: ON
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH2.PHC
Point Name: RECCNTR.AH2.PHC
Point Type: LAO
Descriptor: PREHEAT TMP STPT
Value: 77.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.PHT
Point Name: RECCNTR.AH2.PHT
Point Type: LAI
Descriptor: AH2 PHT COIL TMP
Value: 66.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 140.0
Low Limit: 42.0
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 02 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.PHV
Point Name: RECCNTR.AH2.PHV
Point Type: LAO
Descriptor: AH2 PHT COIL VLV
Value: 16.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.RAF
Point Name: RECCNTR.AH2.RAF
Point Type: L2SL
Descriptor: RELIEF FAN SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
On/Off Point Address: 2 03 24
Inverted: No
Proof Point Address: 2 03 23
Normally Closed: No
Proof Delay: 0 Informational Text
********************************************************************************
Point System Name: RECCNTR.AH2.RAH
Point Name: RECCNTR.AH2.RAH
Point Type: LAI
Descriptor: AH2 RA HUMID
Value: 41.26
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: % RH
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.003255
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.RAT
Point Name: RECCNTR.AH2.RAT
Point Type: LAI
Descriptor: AH2 RA TEMP
Value: 68.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 50.0
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 07 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.RFAN.EAD
Point Name: RECCNTR.AH2.RFAN.EAD
Point Type: L2SL
Descriptor: AH2 RFN EA DMPR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM38
On/Off Point Address: 0 07 02
Inverted: No
Proof Point Address: 0 09 02
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: RECCNTR.AH2.RMS
Point Name: RECCNTR.AH2.RMS
Point Type: LAO
Descriptor: ROOM TEMP STPT
Value: 68.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.RMT
Point Name: RECCNTR.AH2.RMT
Point Type: LAI
Descriptor: AH2 ROOM TEMP
Value: 68.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 55.0
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 07 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.RVF
Point Name: RECCNTR.AH2.RVF
Point Type: LAO
Descriptor: AH2 EX FN SPEED
Value: 32.51
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 03 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.SAC
Point Name: RECCNTR.AH2.SAC
Point Type: LAO
Descriptor: SPLY TEMP STPT
Value: 61.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH2.SAF
Point Name: RECCNTR.AH2.SAF
Point Type: LDO
Descriptor: SPLY START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 1 01 24
Inverted: No
********************************************************************************
Point System Name: RECCNTR.AH2.SAT
Point Name: RECCNTR.AH2.SAT
Point Type: LAI
Descriptor: AH2 SA TEMP
Value: 66.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 140.0
Low Limit: 42.0
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 02 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.SEA
Point Name: RECCNTR.AH2.SEA
Point Type: LDO
Descriptor: HT CL SEASON
Value: HEAT
Condition: -N-
Priority: NONE
Text Table: COOL_HEAT
0 - COOL
1 - HEAT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH2.SMKSAP
Point Name: RECCNTR.AH2.SMKSAP
Point Type: LDI
Descriptor: SMK/HI STATIC AL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 07 08
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.AH2.SPF
Point Name: RECCNTR.AH2.SPF
Point Type: LDI
Descriptor: FAN PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 0 07 06
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH2.SVF
Point Name: RECCNTR.AH2.SVF
Point Type: LAO
Descriptor: AH2 SUPPLY SPEED
Value: 60.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: 1 01 53
Actuator Type Voltage
Slope: 0.006104
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH2.WUP
Point Name: RECCNTR.AH2.WUP
Point Type: LDO
Descriptor: WARM UP MODE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH3.CCV
Point Name: RECCNTR.AH3.CCV
Point Type: LAO
Descriptor: AH3 CLG COIL VLV
Value: 6.96
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.DMN
Point Name: RECCNTR.AH3.DMN
Point Type: LAO
Descriptor: DAMPER MIN POS
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.EAD
Point Name: RECCNTR.AH3.EAD
Point Type: LAO
Descriptor: AH3 EA DAMPER
Value: 14.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.ERR
Point Name: RECCNTR.AH3.ERR
Point Type: LAO
Descriptor: SPLY TMP ERROR
Value: 2.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.FAULT.RVFD
Point Name: RECCNTR.AH3.FAULT.RVFD
Point Type: LDI
Descriptor: RETURN VFD FAULT
Value: NORMAL
Condition: -N-
Priority: NONE
Text Table: NORMAL_ALARM
0 - NORMAL
1 - ALARM
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: 2 02 92
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH3.FAULT.SVFD
Point Name: RECCNTR.AH3.FAULT.SVFD
Point Type: LDI
Descriptor: SUPPLY VFD FAULT
Value: NORMAL
Condition: -N-
Priority: NONE
Text Table: NORMAL_ALARM
0 - NORMAL
1 - ALARM
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: 2 01 92
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH3.FCM
Point Name: RECCNTR.AH3.FCM
Point Type: LDO
Descriptor: FREE CLG MODE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH3.FLT
Point Name: RECCNTR.AH3.FLT
Point Type: LAI
Descriptor: AH3 FILTER DP
Value: 0.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 02 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000102
Intercept: -0.62512
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.FRZ
Point Name: RECCNTR.AH3.FRZ
Point Type: LDI
Descriptor: AH3 FREEZESTAT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 09 03
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH3.HCT
Point Name: RECCNTR.AH3.HCT
Point Type: LAI
Descriptor: AH3 HTG COIL TMP
Value: 68.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 02 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.HCV
Point Name: RECCNTR.AH3.HCV
Point Type: LAO
Descriptor: AH3 HTG COIL VLV
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.HLSAP
Point Name: RECCNTR.AH3.HLSAP
Point Type: LDI
Descriptor: AH3 HI LO PRESSR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 09 04
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.AH3.LPO
Point Name: RECCNTR.AH3.LPO
Point Type: LAO
Descriptor: SUPPLY LOOP
Value: 59.71
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.MAC
Point Name: RECCNTR.AH3.MAC
Point Type: LAO
Descriptor: MIXED TEMP STPT
Value: 58.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.MAD
Point Name: RECCNTR.AH3.MAD
Point Type: LAO
Descriptor: AH3 MA DAMPER
Value: 14.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.MAT
Point Name: RECCNTR.AH3.MAT
Point Type: LAI
Descriptor: AH3 MA TEMP
Value: 67.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 02 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.MN1
Point Name: RECCNTR.AH3.MN1
Point Type: LAO
Descriptor: MIN1 ROOM TEMP
Value: 65.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.MNT
Point Name: RECCNTR.AH3.MNT
Point Type: LAO
Descriptor: MIN ROOM TEMP
Value: 65.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.MS1
Point Name: RECCNTR.AH3.MS1
Point Type: LAO
Descriptor: MIXED STPT 1
Value: 46.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.MS2
Point Name: RECCNTR.AH3.MS2
Point Type: LAO
Descriptor: MIXED STPT 2
Value: 64.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.NMBR.CLG
Point Name: RECCNTR.AH3.NMBR.CLG
Point Type: LAO
Descriptor: NMBR REQ CLG
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: NMBR
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.OCC
Point Name: RECCNTR.AH3.OCC
Point Type: LDO
Descriptor: OCC UNOCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH3.RACFM
Point Name: RECCNTR.AH3.RACFM
Point Type: LAI
Descriptor: AH3 RA CFM
Value: 0.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 02 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25011
COV Limit: 0.005
********************************************************************************
Point System Name: RECCNTR.AH3.RAE
Point Name: RECCNTR.AH3.RAE
Point Type: LAO
Descriptor: RTRN ENTHALPY
Value: 22.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.RAF
Point Name: RECCNTR.AH3.RAF
Point Type: LDO
Descriptor: START/STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: REC.PXCM37
Point Address: 2 02 24
Inverted: No
********************************************************************************
Point System Name: RECCNTR.AH3.RAH
Point Name: RECCNTR.AH3.RAH
Point Type: LAI
Descriptor: AH3 RA HUMID
Value: 38.81
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: % RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.RAT
Point Name: RECCNTR.AH3.RAT
Point Type: LAI
Descriptor: AH3 RA TEMP
Value: 69.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 50.0
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.45999
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.RCFM
Point Name: RECCNTR.AH3.RCFM
Point Type: LAO
Descriptor: RTRN AIR FLOW
Value: 9478.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.RFC
Point Name: RECCNTR.AH3.RFC
Point Type: LAO
Descriptor: RTRN CFM STPT
Value: 9.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.RPF
Point Name: RECCNTR.AH3.RPF
Point Type: LDI
Descriptor: RETURN PROOF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 09 02
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH3.RVF
Point Name: RECCNTR.AH3.RVF
Point Type: LAO
Descriptor: AH3 RETURN SPEED
Value: 35.63
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 2 02 53
Actuator Type Voltage
Slope: 0.006104
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.SAC
Point Name: RECCNTR.AH3.SAC
Point Type: LAO
Descriptor: SPLY TEMP STPT
Value: 63.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.SACFM
Point Name: RECCNTR.AH3.SACFM
Point Type: LAI
Descriptor: AH3 SA CFM
Value: 0.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 02 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25011
COV Limit: 0.001
********************************************************************************
Point System Name: RECCNTR.AH3.SAF
Point Name: RECCNTR.AH3.SAF
Point Type: LDO
Descriptor: START/STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: REC.PXCM37
Point Address: 2 01 24
Inverted: No
********************************************************************************
Point System Name: RECCNTR.AH3.SAP
Point Name: RECCNTR.AH3.SAP
Point Type: LAI
Descriptor: AH3 SA STATIC
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 02 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24996
COV Limit: 0.1
********************************************************************************
Point System Name: RECCNTR.AH3.SAT
Point Name: RECCNTR.AH3.SAT
Point Type: LAI
Descriptor: AH3 SA TEMP
Value: 61.32
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 50.0
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.SCFM
Point Name: RECCNTR.AH3.SCFM
Point Type: LAO
Descriptor: SPLY AIR FLOW
Value: 12437.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 250.0
********************************************************************************
Point System Name: RECCNTR.AH3.SEA
Point Name: RECCNTR.AH3.SEA
Point Type: LDO
Descriptor: HT CL SEASON
Value: COOL
Condition: -N-
Priority: NONE
Text Table: COOL_HEAT
0 - COOL
1 - HEAT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH3.SFC
Point Name: RECCNTR.AH3.SFC
Point Type: LAO
Descriptor: SPLY CFM STPT
Value: 11.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH3.SMK
Point Name: RECCNTR.AH3.SMK
Point Type: LDI
Descriptor: AH3 SMOKE ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 09 05
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.AH3.SPF
Point Name: RECCNTR.AH3.SPF
Point Type: LDI
Descriptor: SUPPLY PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 2 01 23
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH3.SSC
Point Name: RECCNTR.AH3.SSC
Point Type: LAO
Descriptor: STATIC SETPT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.05
********************************************************************************
Point System Name: RECCNTR.AH3.SVF
Point Name: RECCNTR.AH3.SVF
Point Type: LAO
Descriptor: AH3 SUPPLY SPEED
Value: 60.78
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 2 01 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH3.WUP
Point Name: RECCNTR.AH3.WUP
Point Type: LDO
Descriptor: WARM UP MODE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH4.CCV
Point Name: RECCNTR.AH4.CCV
Point Type: LAO
Descriptor: AH4 CLG COIL VLV
Value: 10.26
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 01 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.DMN
Point Name: RECCNTR.AH4.DMN
Point Type: LAO
Descriptor: DAMPER MIN POS
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.EAD
Point Name: RECCNTR.AH4.EAD
Point Type: LAO
Descriptor: AH4 EA DAMPER
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.EAP
Point Name: RECCNTR.AH4.EAP
Point Type: LAI
Descriptor: RETURN PRESSURE
Value: 0.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INH2O
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 10 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.75
COV Limit: 0.01
********************************************************************************
Point System Name: RECCNTR.AH4.ERR
Point Name: RECCNTR.AH4.ERR
Point Type: LAO
Descriptor: SUPPLY TMP ERROR
Value: 3.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.FAULT.RVFD
Point Name: RECCNTR.AH4.FAULT.RVFD
Point Type: LDI
Descriptor: RETURN VFD FAULT
Value: NORMAL
Condition: -N-
Priority: NONE
Text Table: NORMAL_ALARM
0 - NORMAL
1 - ALARM
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 02 93
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH4.FAULT.SVFD
Point Name: RECCNTR.AH4.FAULT.SVFD
Point Type: LDI
Descriptor: RETURN VFD FAULT
Value: NORMAL
Condition: -N-
Priority: NONE
Text Table: NORMAL_ALARM
0 - NORMAL
1 - ALARM
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 01 92
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH4.FCM
Point Name: RECCNTR.AH4.FCM
Point Type: LDO
Descriptor: FREE CLG MODE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH4.FLT
Point Name: RECCNTR.AH4.FLT
Point Type: LAI
Descriptor: AH4 FILTER DP
Value: 0.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000102
Intercept: -0.62512
COV Limit: 0.1
********************************************************************************
Point System Name: RECCNTR.AH4.FRZ
Point Name: RECCNTR.AH4.FRZ
Point Type: LDI
Descriptor: AH4 FREEZESTAT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 09 04
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.AH4.HCT
Point Name: RECCNTR.AH4.HCT
Point Type: LAI
Descriptor: AH4.HTG COIL TMP
Value: 66.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 140.0
Low Limit: 42.0
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17239
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.HCV
Point Name: RECCNTR.AH4.HCV
Point Type: LAO
Descriptor: AH4 HTG COIL VLV
Value: 12.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 01 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.HLSAP
Point Name: RECCNTR.AH4.HLSAP
Point Type: LDI
Descriptor: AH4 HI STATIC AL
Value: NORMAL
Condition: -N-
Priority: NONE
Text Table: NORMAL_ALARM
0 - NORMAL
1 - ALARM
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 09 05
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.AH4.HRC.HRP1
Point Name: RECCNTR.AH4.HRC.HRP1
Point Type: L2SL
Descriptor: HEAT RCVR PUMP 1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM38
On/Off Point Address: 0 07 03
Inverted: No
Proof Point Address: 0 09 03
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.AH4.HRC.HWC
Point Name: RECCNTR.AH4.HRC.HWC
Point Type: LAO
Descriptor: HRC TEMP STPT
Value: 53.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.HRC.HWT
Point Name: RECCNTR.AH4.HRC.HWT
Point Type: LAI
Descriptor: AH4 HRC HWT
Value: 72.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 45.0
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 08 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 5.0
********************************************************************************
Point System Name: RECCNTR.AH4.HRC.VLV
Point Name: RECCNTR.AH4.HRC.VLV
Point Type: LAO
Descriptor: AH4 HRC VALVE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.LPO
Point Name: RECCNTR.AH4.LPO
Point Type: LAO
Descriptor: SUPPLY LOOP
Value: 51.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.MAC
Point Name: RECCNTR.AH4.MAC
Point Type: LAO
Descriptor: MIXED TEMP STPT
Value: 59.35
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.MAD
Point Name: RECCNTR.AH4.MAD
Point Type: LAO
Descriptor: AH4 MA DAMPERS
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.MAT
Point Name: RECCNTR.AH4.MAT
Point Type: LAI
Descriptor: AH4 MA TEMP
Value: 67.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 30.0
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17239
COV Limit: 5.0
********************************************************************************
Point System Name: RECCNTR.AH4.MAX1
Point Name: RECCNTR.AH4.MAX1
Point Type: LAO
Descriptor: MAX1 RM ERROR
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.MN1
Point Name: RECCNTR.AH4.MN1
Point Type: LAO
Descriptor: MIN1 RM ERROR
Value: -4.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.MNRER
Point Name: RECCNTR.AH4.MNRER
Point Type: LAO
Descriptor: MIN ROOM ERROR
Value: -4.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.MOACFM
Point Name: RECCNTR.AH4.MOACFM
Point Type: LAI
Descriptor: MN OA FLOW DP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00001
Intercept: -0.0626
COV Limit: 0.1
********************************************************************************
Point System Name: RECCNTR.AH4.MOAD
Point Name: RECCNTR.AH4.MOAD
Point Type: LAO
Descriptor: AH4 MIN OA DMPR
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.MXRER
Point Name: RECCNTR.AH4.MXRER
Point Type: LAO
Descriptor: MAX ROOM ERROR
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.NMBR.CLG
Point Name: RECCNTR.AH4.NMBR.CLG
Point Type: LAO
Descriptor: NMBR REQ CLG
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: NMBR
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.OACFM
Point Name: RECCNTR.AH4.OACFM
Point Type: LAO
Descriptor: IN OA INTAKE CFM
Value: 304.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 20.0
********************************************************************************
Point System Name: RECCNTR.AH4.OCC
Point Name: RECCNTR.AH4.OCC
Point Type: LDO
Descriptor: OCC UNOCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH4.RAE
Point Name: RECCNTR.AH4.RAE
Point Type: LAO
Descriptor: RTRN ENTHALPY
Value: 25.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.RAF
Point Name: RECCNTR.AH4.RAF
Point Type: LDO
Descriptor: START/STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: REC.PXCM38
Point Address: 2 02 24
Inverted: No
********************************************************************************
Point System Name: RECCNTR.AH4.RAH
Point Name: RECCNTR.AH4.RAH
Point Type: LAI
Descriptor: AH4 RA HUMID
Value: 44.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: % RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.RAT
Point Name: RECCNTR.AH4.RAT
Point Type: LAI
Descriptor: AH4 RA TEMP
Value: 72.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 55.0
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 08 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17239
COV Limit: 5.0
********************************************************************************
Point System Name: RECCNTR.AH4.RPF
Point Name: RECCNTR.AH4.RPF
Point Type: LDI
Descriptor: RETURN PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 02 23
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH4.RVF
Point Name: RECCNTR.AH4.RVF
Point Type: LAO
Descriptor: AH4 RETURN SPEED
Value: 0.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 02 53
Actuator Type Voltage
Slope: 0.00631
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.SAC
Point Name: RECCNTR.AH4.SAC
Point Type: LAO
Descriptor: SUPPLY TEMP STPT
Value: 65.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.SAF
Point Name: RECCNTR.AH4.SAF
Point Type: LDO
Descriptor: START/STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: REC.PXCM38
Point Address: 2 01 24
Inverted: No
********************************************************************************
Point System Name: RECCNTR.AH4.SAP
Point Name: RECCNTR.AH4.SAP
Point Type: LAI
Descriptor: AH4 SA PRESS
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24996
COV Limit: 0.1
********************************************************************************
Point System Name: RECCNTR.AH4.SAT
Point Name: RECCNTR.AH4.SAT
Point Type: LAI
Descriptor: AH4.SA TEMP
Value: 63.63
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 140.0
Low Limit: 42.0
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 08 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17239
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.AH4.SEA
Point Name: RECCNTR.AH4.SEA
Point Type: LDO
Descriptor: HT CL SEASON
Value: COOL
Condition: -N-
Priority: NONE
Text Table: COOL_HEAT
0 - COOL
1 - HEAT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.AH4.SMK
Point Name: RECCNTR.AH4.SMK
Point Type: LDI
Descriptor: AH4 SMOKE ALM
Value: NORMAL
Condition: -N-
Priority: NONE
Text Table: NORMAL_ALARM
0 - NORMAL
1 - ALARM
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 09 06
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.AH4.SPF
Point Name: RECCNTR.AH4.SPF
Point Type: LDI
Descriptor: SUPPLY PROOF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 01 23
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.AH4.SSC
Point Name: RECCNTR.AH4.SSC
Point Type: LAO
Descriptor: DUCT STATIC STPT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.05
********************************************************************************
Point System Name: RECCNTR.AH4.SSP
Point Name: RECCNTR.AH4.SSP
Point Type: LAI
Descriptor: AH4 SPACE PRESS
Value: 0.0257
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: IN WC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: -0.37371
COV Limit: 0.01
********************************************************************************
Point System Name: RECCNTR.AH4.SSPC
Point Name: RECCNTR.AH4.SSPC
Point Type: LAO
Descriptor: SPACE STATIC SPT
Value: 0.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 3
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.01
********************************************************************************
Point System Name: RECCNTR.AH4.SVF
Point Name: RECCNTR.AH4.SVF
Point Type: LAO
Descriptor: AH3 SUPPLY SPEED
Value: 0.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 2 01 53
Actuator Type Voltage
Slope: 0.006104
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.AH4.WUP
Point Name: RECCNTR.AH4.WUP
Point Type: LDO
Descriptor: WARM UP MODE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.BLDGPRES
Point Name: RECCNTR.BLDGPRES
Point Type: LAI
Descriptor: BLDG PRESS
Value: 0.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 02 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: -0.37491
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.BLDGPRES.STPT
Point Name: RECCNTR.BLDGPRES.STPT
Point Type: LAO
Descriptor: STATIC SETPOINT
Value: 0.04
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: RECCNTR.BRM037
Point Name: RECCNTR.BRM037
Point Type: LAO
Descriptor: VIR OA BAROMETER
Value: 29.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.BRM038
Point Name: RECCNTR.BRM038
Point Type: LAO
Descriptor: VIR OA BAROMETER
Value: 29.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.CHW.ALM
Point Name: RECCNTR.CHW.ALM
Point Type: LDO
Descriptor: CRITICL PMP FAIL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.CHW.ALT
Point Name: RECCNTR.CHW.ALT
Point Type: LDO
Descriptor: PUMP ALTERNATE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.CHW.CHWRT
Point Name: RECCNTR.CHW.CHWRT
Point Type: LAI
Descriptor: CHWR TEMP
Value: 61.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 08 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.CHWST
Point Name: RECCNTR.CHW.CHWST
Point Type: LAI
Descriptor: CHWS TEMP
Value: 50.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 08 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.DLT
Point Name: RECCNTR.CHW.DLT
Point Type: LAO
Descriptor: DELTA TEMP
Value: 11.59
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.DLY
Point Name: RECCNTR.CHW.DLY
Point Type: LAO
Descriptor: PREV DAY USEAGE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.DP
Point Name: RECCNTR.CHW.DP
Point Type: LAI
Descriptor: CHW DIFF PRESS
Value: 13.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.002035
Intercept: -12.49993
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.DPV
Point Name: RECCNTR.CHW.DPV
Point Type: LAO
Descriptor: CHW DP VALVE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: RECCNTR.CHW.ENA
Point Name: RECCNTR.CHW.ENA
Point Type: LDO
Descriptor: CW SYSTEM ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.CHW.GPM
Point Name: RECCNTR.CHW.GPM
Point Type: LAI
Descriptor: CHW GPM FLOW
Value: -0.37
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.024414
Intercept: -150.0
COV Limit: 50.0
********************************************************************************
Point System Name: RECCNTR.CHW.MTD
Point Name: RECCNTR.CHW.MTD
Point Type: LAO
Descriptor: MONTH TO DATE
Value: 39536.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.MTR
Point Name: RECCNTR.CHW.MTR
Point Type: LAO
Descriptor: CALCULATED TONS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: Minutes
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.PMT
Point Name: RECCNTR.CHW.PMT
Point Type: LAO
Descriptor: PREVIUOS MONTH
Value: 583607.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.PP1
Point Name: RECCNTR.CHW.PP1
Point Type: L2SL
Descriptor: CHW PMP1 SS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM37
On/Off Point Address: 0 07 02
Inverted: No
Proof Point Address: 0 09 06
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.CHW.PP2
Point Name: RECCNTR.CHW.PP2
Point Type: L2SL
Descriptor: CHW PMP2 SS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM37
On/Off Point Address: 0 07 01
Inverted: No
Proof Point Address: 0 09 07
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.CHW.PYR
Point Name: RECCNTR.CHW.PYR
Point Type: LAO
Descriptor: PREVIUOS YEAR
Value: 3578316.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CHW.RPT
Point Name: RECCNTR.CHW.RPT
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.CHW.RPT1
Point Name: RECCNTR.CHW.RPT1
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.CHW.YTD
Point Name: RECCNTR.CHW.YTD
Point Type: LAO
Descriptor: YEAR TO DATE
Value: 3593802.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: TONS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.CTLAIR.LPA
Point Name: RECCNTR.CTLAIR.LPA
Point Type: LDI
Descriptor: CNTRL AIR LP ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 09 11
Normally Closed: Yes
********************************************************************************
Point System Name: RECCNTR.DWH1.HWCV
Point Name: RECCNTR.DWH1.HWCV
Point Type: LAO
Descriptor: CONTROL VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 08
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: RECCNTR.DWH1.HWSC
Point Name: RECCNTR.DWH1.HWSC
Point Type: LAO
Descriptor: HOT WATER SETPT
Value: 120.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.DWH1.HWST
Point Name: RECCNTR.DWH1.HWST
Point Type: LAI
Descriptor: DOM HWTR STMP
Value: 133.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 08 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.DWH1.PP1
Point Name: RECCNTR.DWH1.PP1
Point Type: L2SL
Descriptor: DOM HWTR PMP1
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM37
On/Off Point Address: 0 07 03
Inverted: No
Proof Point Address: 0 09 08
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.DWH2.HWCV
Point Name: RECCNTR.DWH2.HWCV
Point Type: LAO
Descriptor: CONTROL VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 07
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: RECCNTR.DWH2.HWSC
Point Name: RECCNTR.DWH2.HWSC
Point Type: LAO
Descriptor: HOT WATER SETPT
Value: 120.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.DWH2.HWST
Point Name: RECCNTR.DWH2.HWST
Point Type: LAI
Descriptor: LNDRY HWS TMP
Value: 124.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 08 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.DWH2.PP2
Point Name: RECCNTR.DWH2.PP2
Point Type: L2SL
Descriptor: LNDRY HWTR PMP2
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM37
On/Off Point Address: 0 07 04
Inverted: No
Proof Point Address: 0 09 09
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.E.TEST
Point Name: RECCNTR.E.TEST
Point Type: LPACI
Descriptor: LPACI
Value: 827608.375
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 4
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 08 05
Gain: 0.8
Count Both Edges: No
COV Limit: 0.8
********************************************************************************
Point System Name: RECCNTR.EF1
Point Name: RECCNTR.EF1
Point Type: L2SL
Descriptor: EF1 START STOP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM38
On/Off Point Address: 0 07 04
Inverted: No
Proof Point Address: 0 09 07
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.EF2
Point Name: RECCNTR.EF2
Point Type: L2SL
Descriptor: EF2 START STOP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM35
On/Off Point Address: 0 07 01
Inverted: No
Proof Point Address: 0 08 03
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.ELEC
Point Name: RECCNTR.ELEC
Point Type: LPACI
Descriptor: LPACI
Value: 954355.3125
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 08 05
Gain: 0.8
Count Both Edges: No
COV Limit: 0.8
********************************************************************************
Point System Name: RECCNTR.ELEC.DEMAND
Point Name: RECCNTR.ELEC.DEMAND
Point Type: LAO
Descriptor: ELECTRIC DEMAND
Value: 89.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.ELEC.METER.READING
Point Name: RECCNTR.ELEC.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 954355.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: RECCNTR.FIRE.ALM
Point Name: RECCNTR.FIRE.ALM
Point Type: LDI
Descriptor: COMMON FIRE ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 09 12
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.GWSUMP.HAL
Point Name: RECCNTR.GWSUMP.HAL
Point Type: LDI
Descriptor: GRND WTR SMP ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 08 04
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.H2O.METER.READING
Point Name: RECCNTR.H2O.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 27415846
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: RECCNTR.HRC.ENA
Point Name: RECCNTR.HRC.ENA
Point Type: LDO
Descriptor: HT RCVRY ENABLE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.HWP1.SS
Point Name: RECCNTR.HWP1.SS
Point Type: L2SL
Descriptor: HWP1 STRT STOP
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
On/Off Point Address: 3 01 24
Inverted: No
Proof Point Address: 3 01 23
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: RECCNTR.HWP2.SPD
Point Name: RECCNTR.HWP2.SPD
Point Type: LAO
Descriptor: HWP 2 SPEED
Value: 63.24
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 3 02 53
Actuator Type Voltage
Slope: 0.00631
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.HWP2.SS
Point Name: RECCNTR.HWP2.SS
Point Type: L2SL
Descriptor: HWP2 STRT STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
On/Off Point Address: 3 02 24
Inverted: No
Proof Point Address: 3 02 23
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: RECCNTR.HX1.ALM
Point Name: RECCNTR.HX1.ALM
Point Type: LDO
Descriptor: CRITICL PMP FAIL
Value: NORMAL
Condition: -N-
Priority: NONE
Text Table: NORMAL_ALARM
0 - NORMAL
1 - ALARM
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.HX1.ALT
Point Name: RECCNTR.HX1.ALT
Point Type: LDO
Descriptor: PUMP ALTERNATE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.HX1.ENA
Point Name: RECCNTR.HX1.ENA
Point Type: LDO
Descriptor: HEAT EXCH ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.HX1.HWRT
Point Name: RECCNTR.HX1.HWRT
Point Type: LAI
Descriptor: HX1 HWR TEMP
Value: 156.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.HX1.HWSC
Point Name: RECCNTR.HX1.HWSC
Point Type: LAO
Descriptor: HEAT WATER SETPT
Value: 160.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.HX1.HWST
Point Name: RECCNTR.HX1.HWST
Point Type: LAI
Descriptor: HX1 HWS TEMP
Value: 157.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.17242
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.HX1.LOOPOUT
Point Name: RECCNTR.HX1.LOOPOUT
Point Type: LAO
Descriptor: PRESS LOOPOUT
Value: 63.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.HX1.PRC
Point Name: RECCNTR.HX1.PRC
Point Type: LAO
Descriptor: HX1 PRESS STPT
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSID
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.HX1.PRS
Point Name: RECCNTR.HX1.PRS
Point Type: LAI
Descriptor: HX1 DIFF PRESS
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSID
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 03 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.001017
Intercept: -6.25011
COV Limit: 0.1
********************************************************************************
Point System Name: RECCNTR.HX1.PUMP.LEAD
Point Name: RECCNTR.HX1.PUMP.LEAD
Point Type: LDO
Descriptor: HOT WTR PMP LDLG
Value: P2 LEAD
Condition: -N-
Priority: NONE
Text Table: REC_HX_PUMP_LEAD
0 - P2 LEAD
1 - P1 LEAD
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.HX1.VLVS
Point Name: RECCNTR.HX1.VLVS
Point Type: LAO
Descriptor: HX1 CNTRL VLVS
Value: 12.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 01 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.LAST.MONTH.ELEC.CONSUM
Point Name: RECCNTR.LAST.MONTH.ELEC.CONSUM
Point Type: LAO
Descriptor:
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.LAST.MONTH.H2O.CONSUMP
Point Name: RECCNTR.LAST.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST MNTH CONSMP
Value: 89444
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.LAST.WEEK.ELEC.CONSUMP
Point Name: RECCNTR.LAST.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor:
Value: 12096.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.LAST.WEEK.H2O.CONSUMP
Point Name: RECCNTR.LAST.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 18126
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.LNDRY.DMPR
Point Name: RECCNTR.LNDRY.DMPR
Point Type: LDO
Descriptor: LAUNDRY DAMPER
Value: OPEN
Condition: -N-
Priority: NONE
Text Table: OPEN_CLOSED
0 - OPEN
1 - CLOSED
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 07 05
Inverted: No
********************************************************************************
Point System Name: RECCNTR.LNDRY.DRYER1
Point Name: RECCNTR.LNDRY.DRYER1
Point Type: LDI
Descriptor: DRYER1 STATUS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 09 08
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.LNDRY.DRYER2
Point Name: RECCNTR.LNDRY.DRYER2
Point Type: LDI
Descriptor: DRYER2 STATUS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 0 09 09
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.MONTH.ELEC.CONSUMP
Point Name: RECCNTR.MONTH.ELEC.CONSUMP
Point Type: LAO
Descriptor:
Value: 31266664.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.MONTH.H2O.CONSUMP
Point Name: RECCNTR.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: THIS MNTH CONSMP
Value: 38958
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.NE.HEAT.TAPE
Point Name: RECCNTR.NE.HEAT.TAPE
Point Type: LDO
Descriptor: NE HEAT TAPE
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: 1 23 45
Inverted: No
********************************************************************************
Point System Name: RECCNTR.NW.HEAT.TAPE
Point Name: RECCNTR.NW.HEAT.TAPE
Point Type: LDO
Descriptor: NW HEAT TAPE
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 1 10 45
Inverted: No
********************************************************************************
Point System Name: RECCNTR.OAE037
Point Name: RECCNTR.OAE037
Point Type: LAO
Descriptor: VIR OA ENTHALPY
Value: 20.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.OAE038
Point Name: RECCNTR.OAE038
Point Type: LAO
Descriptor: VIR OA ENTHALPY
Value: 20.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.OAH037
Point Name: RECCNTR.OAH037
Point Type: LAO
Descriptor: VIR OA HUMIDITY
Value: 47.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.OAH038
Point Name: RECCNTR.OAH038
Point Type: LAO
Descriptor: VIR OA HUMIDITY
Value: 47.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.OAT035
Point Name: RECCNTR.OAT035
Point Type: LAO
Descriptor: VIR OA TEMP
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.OAT036
Point Name: RECCNTR.OAT036
Point Type: LAO
Descriptor: VIR OA TEMP
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM36
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.OAT037
Point Name: RECCNTR.OAT037
Point Type: LAO
Descriptor: VIR OA TEMP
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.OAT038
Point Name: RECCNTR.OAT038
Point Type: LAO
Descriptor: VIR OA TEMP
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: RECCNTR.SE.HEAT.TAPE
Point Name: RECCNTR.SE.HEAT.TAPE
Point Type: LDO
Descriptor: SE HEAT TAPE
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 1 20 45
Inverted: No
********************************************************************************
Point System Name: RECCNTR.SF5
Point Name: RECCNTR.SF5
Point Type: L2SL
Descriptor: SF5 STR STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: REC.PXCM37
On/Off Point Address: 0 07 05
Inverted: No
Proof Point Address: 0 09 10
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: RECCNTR.STEAM.DLY
Point Name: RECCNTR.STEAM.DLY
Point Type: LAO
Descriptor: PREV DAY USEAGE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.STEAM.MTD
Point Name: RECCNTR.STEAM.MTD
Point Type: LAO
Descriptor: MONTH TO DATE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.STEAM.PMT
Point Name: RECCNTR.STEAM.PMT
Point Type: LAO
Descriptor: PREVIOUS MONTH
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.STEAM.PYR
Point Name: RECCNTR.STEAM.PYR
Point Type: LAO
Descriptor: PREVIOUS YEAR
Value: 18610.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.STEAM.RPT
Point Name: RECCNTR.STEAM.RPT
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.STEAM.RPT1
Point Name: RECCNTR.STEAM.RPT1
Point Type: LDO
Descriptor: REPEAT AVOIDENCE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
********************************************************************************
Point System Name: RECCNTR.STEAM.YTD
Point Name: RECCNTR.STEAM.YTD
Point Type: LAO
Descriptor: YEAR TO DATE
Value: 40.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.STMPRS
Point Name: RECCNTR.STMPRS
Point Type: LAI
Descriptor: STEAM PRESS
Value: 8.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Standard Alarms
High Limit: 20.0
Low Limit: 5.0
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.001221
Intercept: -7.50007
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.SW.HEAT.TAPE
Point Name: RECCNTR.SW.HEAT.TAPE
Point Type: LDO
Descriptor: SW HEAT TAPE
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: 1 18 45
Inverted: No
********************************************************************************
Point System Name: RECCNTR.TODAY.EL.CONSUMP
Point Name: RECCNTR.TODAY.EL.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 2951.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.TODAY.ELEC.CONSUMP
Point Name: RECCNTR.TODAY.ELEC.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 1063.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.TODAY.H2O.CONSUMP
Point Name: RECCNTR.TODAY.H2O.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 942
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.TRANSFER.ALM
Point Name: RECCNTR.TRANSFER.ALM
Point Type: LDI
Descriptor: TRANSFER SW ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: REC.PXCM37
Point Address: 0 09 13
Normally Closed: No
********************************************************************************
Point System Name: RECCNTR.VAV4.01.ERR
Point Name: RECCNTR.VAV4.01.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -4.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.02.ERR
Point Name: RECCNTR.VAV4.02.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: 0.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.03.ERR
Point Name: RECCNTR.VAV4.03.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -3.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.04.ERR
Point Name: RECCNTR.VAV4.04.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.05.ERR
Point Name: RECCNTR.VAV4.05.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.06.ERR
Point Name: RECCNTR.VAV4.06.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: 0.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.07.ERR
Point Name: RECCNTR.VAV4.07.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.08.ERR
Point Name: RECCNTR.VAV4.08.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.09.ERR
Point Name: RECCNTR.VAV4.09.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -0.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.10.ERR
Point Name: RECCNTR.VAV4.10.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -0.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.11.ERR
Point Name: RECCNTR.VAV4.11.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -0.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.12.ERR
Point Name: RECCNTR.VAV4.12.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -0.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.13.ERR
Point Name: RECCNTR.VAV4.13.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: 0.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.VAV4.14.ERR
Point Name: RECCNTR.VAV4.14.ERR
Point Type: LAO
Descriptor: RM SETPT ERROR
Value: -4.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM38
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.WATER.DEMAND
Point Name: RECCNTR.WATER.DEMAND
Point Type: LAO
Descriptor: NOURSE H2O DEMND
Value: 104.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.WATER.HI
Point Name: RECCNTR.WATER.HI
Point Type: LPACI
Descriptor: LPACI
Value: 26725600.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 01 07
Gain: 100.0
Count Both Edges: No
COV Limit: 100.0
********************************************************************************
Point System Name: RECCNTR.WATER.HIGH
Point Name: RECCNTR.WATER.HIGH
Point Type: LAO
Descriptor: PDL WATER HIGH
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.WATER.LO
Point Name: RECCNTR.WATER.LO
Point Type: LPACI
Descriptor: LPACI
Value: 690247.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: 0 01 06
Gain: 1.0
Count Both Edges: No
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.WATER.LOW
Point Name: RECCNTR.WATER.LOW
Point Type: LAO
Descriptor: PDL WATER LOW
Value: 104.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.WEEK.EL.CONSUMP
Point Name: RECCNTR.WEEK.EL.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 16084.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.WEEK.ELEC.CONSUMP
Point Name: RECCNTR.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.WEEK.H2O.CONSUMP
Point Name: RECCNTR.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.YEST.EL.CONSUMP
Point Name: RECCNTR.YEST.EL.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 8080.35
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.YEST.ELEC.CONSUMP
Point Name: RECCNTR.YEST.ELEC.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 1484.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM37
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: RECCNTR.YEST.H2O.CONSUMP
Point Name: RECCNTR.YEST.H2O.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 1068
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: REC.PXCM35
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
******************************** End of Report *********************************

## Olin
10/16/2017 Carleton College 03:12 PM
Panel Point Definition Report
Selection: O*
Point System Name: OLD MUSIC ELECTRIC:PPCL Address
Point Name: OLD MUSIC ELECTRIC:PPCL Address
Point Type: LAI
Descriptor:
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: OLDMUSI.LAST.MONTH.EL.CONSUM
Point Name: OLDMUSI.LAST.MONTH.EL.CONSUM
Point Type: LAO
Descriptor:
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.E.TEST
Point Name: OLDMUSIC.E.TEST
Point Type: LPACI
Descriptor:
Value: 51294.3945
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 12 05
Gain: 0.8
Count Both Edges: No
COV Limit: 0.8
Point System Name: OLDMUSIC.EL.CONSUMP
Point Name: OLDMUSIC.EL.CONSUMP
Point Type: LAO
Descriptor:
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.ELEC
Point Name: OLDMUSIC.ELEC
Point Type: LPACI
Descriptor: LPACI
Value: 81243.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 12 05
Gain: 0.8
Count Both Edges: No
COV Limit: 1.0
Point System Name: OLDMUSIC.ELEC.DEMAND
Point Name: OLDMUSIC.ELEC.DEMAND
Point Type: LAO
Descriptor: ELECTRIC DEMAND
Value: 8.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.ELEC.METER.READING
Point Name: OLDMUSIC.ELEC.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 81243.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OLDMUSIC.LAST.MONTH.EL.CONSUM
Point Name: OLDMUSIC.LAST.MONTH.EL.CONSUM
Point Type: LAO
Descriptor: LAST MNTH ELEC
Value: 7924.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OLDMUSIC.LAST.WEEK.EL.CONSUMP
Point Name: OLDMUSIC.LAST.WEEK.EL.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 1564.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.MONTH.EL.CONSUM
Point Name: OLDMUSIC.MONTH.EL.CONSUM
Point Type: LAO
Descriptor:
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.MONTH.EL.CONSUMP
Point Name: OLDMUSIC.MONTH.EL.CONSUMP
Point Type: LAO
Descriptor:
Value: 3484.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.TODAY.EL.CONSUMP
Point Name: OLDMUSIC.TODAY.EL.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 128.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.WEEK.EL.CONSUMP
Point Name: OLDMUSIC.WEEK.EL.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDMUSIC.YEST.EL.CONSUMP
Point Name: OLDMUSIC.YEST.EL.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 173.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OATEST
Point Name: OATEST
Point Type: LAO
Descriptor:
Value: 61.9362
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SS.PXCM03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
Point System Name: OLD.TOWERS
Point Name: OLD.TOWERS
Point Type: LDO
Descriptor: GO BACK TO OLD
Value: OFF
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SS.PXCM21
Point Address: -Virtual-
Point System Name: OL.EF1.ZON:MODE
Point Name: OL.EF1.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OL.EF6.ZON:MODE
Point Name: OL.EF6.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OL.EF7.ZON:MODE
Point Name: OL.EF7.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OL.GENRUN
Point Name: OL.GENRUN
Point Type: LDO
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 01 04
Inverted: No
Point System Name: OL.PNL09.SHEDTMR
Point Name: OL.PNL09.SHEDTMR
Point Type: LAO
Descriptor: MBC09 SHED TIMER
Value: 20300620.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL9OCC
Point Name: OL9OCC
Point Type: LDO
Descriptor: CAB9 TO CAB8
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLA2:DAY.NGT
Point Name: OLA2:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: *F*
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 21 29
Inverted: No
Point System Name: OLA3:DAY.NGT
Point Name: OLA3:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: *F*
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 20 29
Inverted: No
Point System Name: OLA4CV
Point Name: OLA4CV
Point Type: LAO
Descriptor: COOL VALVE
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA4DA
Point Name: OLA4DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 76.59
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 04 03
Sensor Type: Thermistor 100 KOhm
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA4DC
Point Name: OLA4DC
Point Type: LAO
Descriptor: DAMP CNTRL
Value: 12.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA4HV
Point Name: OLA4HV
Point Type: LAO
Descriptor: HEAT VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA4MS
Point Name: OLA4MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 57.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA4MT
Point Name: OLA4MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 69.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 04 06
Sensor Type: Thermistor 100 KOhm
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA4OC
Point Name: OLA4OC
Point Type: LDO
Descriptor: AHU4 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLA4RS
Point Name: OLA4RS
Point Type: LAO
Descriptor: ROOM SETPNT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA4SS
Point Name: OLA4SS
Point Type: L2SL
Descriptor: AHU 4 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 0 01 01
Inverted: No
Proof Point Address: 0 07 01
Normally Closed: No
Proof Delay: 60 Informational Text
Point System Name: OLA4ST
Point Name: OLA4ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 71.49
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 45.0
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 1.99987
Point System Name: OLA5CV
Point Name: OLA5CV
Point Type: LAO
Descriptor: COOL VALVE
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA5DA
Point Name: OLA5DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 73.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 04 04
Sensor Type: Thermistor 100 KOhm
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA5DC
Point Name: OLA5DC
Point Type: LAO
Descriptor: DAMP CNTRL
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA5HV
Point Name: OLA5HV
Point Type: LAO
Descriptor: HEAT VALVE
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA5MS
Point Name: OLA5MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 57.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA5MT
Point Name: OLA5MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 71.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 95.0
Low Limit: 35.0
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 1.99987
Point System Name: OLA5OC
Point Name: OLA5OC
Point Type: LDO
Descriptor: AHU5 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLA5RS
Point Name: OLA5RS
Point Type: LAO
Descriptor: ROOM 141 SETPNT
Value: 70.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA5SS
Point Name: OLA5SS
Point Type: L2SL
Descriptor: AHU 5 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 0 01 02
Inverted: No
Proof Point Address: 0 07 02
Normally Closed: No
Proof Delay: 60 Informational Text
Point System Name: OLA5ST
Point Name: OLA5ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 72.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 55.0
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -3.9993
COV Limit: 1.99987
Point System Name: OLA6CV
Point Name: OLA6CV
Point Type: LAO
Descriptor: COOL VALVE
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 08
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA6DA
Point Name: OLA6DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 67.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
Point System Name: OLA6DC
Point Name: OLA6DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 05 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA6DS
Point Name: OLA6DS
Point Type: LAO
Descriptor: DIS SETPNT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA6MS
Point Name: OLA6MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 52.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA6MT
Point Name: OLA6MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 65.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 1.99987
Point System Name: OLA6OC
Point Name: OLA6OC
Point Type: LDO
Descriptor: AHU6 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLA6RA
Point Name: OLA6RA
Point Type: LAI
Descriptor: REHEAT TEMP
Value: 72.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 04 05
Sensor Type: Thermistor 100 KOhm
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
Point System Name: OLA6RH
Point Name: OLA6RH
Point Type: LAO
Descriptor: REHEAT VLV
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 06 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA6RS
Point Name: OLA6RS
Point Type: LAO
Descriptor: ROOM SETPNT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA6SS
Point Name: OLA6SS
Point Type: L2SL
Descriptor: AHU 6 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 0 01 03
Inverted: No
Proof Point Address: 0 07 03
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: OLA6ST
Point Name: OLA6ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 70.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 50.0
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 1.0
Point System Name: OLA7:DAY.NGT
Point Name: OLA7:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 01 29
Inverted: No
Point System Name: OLA7CS
Point Name: OLA7CS
Point Type: LAO
Descriptor: TEC CTRL SET
Value: 70.0
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 01 92
Actuator Type Voltage
Slope: 0.25
Intercept: 48.0
COV Limit: 0.25
Point System Name: OLA7CT
Point Name: OLA7CT
Point Type: LAO
Descriptor: TEC CNTL TMP
Value: 72.16
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 01 78
Actuator Type Voltage
Slope: 0.25
Intercept: 48.0
COV Limit: 0.25
Point System Name: OLA7HC
Point Name: OLA7HC
Point Type: LDO
Descriptor: TEC HET COOL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLA7SS
Point Name: OLA7SS
Point Type: LDO
Descriptor: TEC FAN SWIT
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: OLIN.PXCM09
Point Address: 1 01 46
Inverted: No
Point System Name: OLE03C
Point Name: OLE03C
Point Type: LAO
Descriptor: STAT SETPT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.10002
Point System Name: OLE03P
Point Name: OLE03P
Point Type: LAI
Descriptor: DUCT STATIC
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H20
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24912
COV Limit: 0.10003
Point System Name: OLE03R
Point Name: OLE03R
Point Type: LAO
Descriptor: LOOP RAMP
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.10002
Point System Name: OLE03S
Point Name: OLE03S
Point Type: LDO
Descriptor: RMS 306 308
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: OLIN.PXCM09
Point Address: 0 01 05
Inverted: Yes
Point System Name: OLE03SS
Point Name: OLE03SS
Point Type: L2SL
Descriptor: DRIVE SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM09
On/Off Point Address: 3 15 24
Inverted: No
Proof Point Address: 3 15 23
Normally Closed: No
Proof Delay: 60 Informational Text
Point System Name: OLE05B
Point Name: OLE05B
Point Type: LDI
Descriptor: BYPASS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 07 07
Normally Closed: No
Point System Name: OLE05C
Point Name: OLE05C
Point Type: LAO
Descriptor: STAT SETPT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.10002
Point System Name: OLE05F
Point Name: OLE05F
Point Type: LDI
Descriptor: FAULT CONDIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 07 06
Normally Closed: No
Point System Name: OLE05P
Point Name: OLE05P
Point Type: LAI
Descriptor: DUCT STATIC
Value: 1.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H20
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 03 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24912
COV Limit: 0.10003
Point System Name: OLE05R
Point Name: OLE05R
Point Type: LAO
Descriptor: LOOP RAMP
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.10002
Point System Name: OLE05S
Point Name: OLE05S
Point Type: LDO
Descriptor: RMS 2 4 8
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: OLIN.PXCM09
Point Address: 0 01 06
Inverted: Yes
Point System Name: OLE05V
Point Name: OLE05V
Point Type: LAO
Descriptor: SPEED CNTRL
Value: 5.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 06 02
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
Point System Name: OLE09B
Point Name: OLE09B
Point Type: LDI
Descriptor: BYPASS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 07 09
Normally Closed: No
Point System Name: OLE09C
Point Name: OLE09C
Point Type: LAO
Descriptor: STAT SETPT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.10002
Point System Name: OLE09F
Point Name: OLE09F
Point Type: LDI
Descriptor: FAULT CONDIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 07 08
Normally Closed: No
Point System Name: OLE09P
Point Name: OLE09P
Point Type: LAI
Descriptor: DUCT STATIC
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H20
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 04 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24912
COV Limit: 0.10003
Point System Name: OLE09R
Point Name: OLE09R
Point Type: LAO
Descriptor: LOOP RAMP
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.10002
Point System Name: OLE09S
Point Name: OLE09S
Point Type: LDO
Descriptor: RMS 10 12 14
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: OLIN.PXCM09
Point Address: 0 02 02
Inverted: Yes
Point System Name: OLE09V
Point Name: OLE09V
Point Type: LAO
Descriptor: SPEED CNTRL
Value: 9.46
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 06 03
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
Point System Name: OLE10P
Point Name: OLE10P
Point Type: LAI
Descriptor: DUCT STATIC
Value: 2.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H20
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 04 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24912
COV Limit: 0.10003
Point System Name: OLE10S
Point Name: OLE10S
Point Type: L2SL
Descriptor: EX FAN 10
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM09
On/Off Point Address: 0 02 01
Inverted: Yes
Proof Point Address: 0 07 10
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: OLECON
Point Name: OLECON
Point Type: LDO
Descriptor: ECONOMIZE MD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLEF01
Point Name: OLEF01
Point Type: L2SL
Descriptor: 2ND3RD RESTR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 3 33 01
Inverted: No
Proof Point Address: 3 34 01
Normally Closed: No
Proof Delay: 180 Informational Text
Point System Name: OLEF02
Point Name: OLEF02
Point Type: L2SL
Descriptor: RADIOACT STO
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: -Virtual-
Proof Point Address: 3 34 02
Normally Closed: No
Proof Delay: 10 Informational Text
Point System Name: OLEF04
Point Name: OLEF04
Point Type: L2SL
Descriptor: RMS 208 210
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 3 33 02
Inverted: Yes
Proof Point Address: 3 34 03
Normally Closed: No
Proof Delay: 60 Informational Text
Point System Name: OLEF06
Point Name: OLEF06
Point Type: L2SL
Descriptor: 211B 211C
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 3 33 03
Inverted: Yes
Proof Point Address: 3 34 04
Normally Closed: No
Proof Delay: 60 Informational Text
Point System Name: OLEF07
Point Name: OLEF07
Point Type: L2SL
Descriptor: GR RR MISC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 3 33 04
Inverted: No
Proof Point Address: 3 34 05
Normally Closed: No
Proof Delay: 60 Informational Text
Point System Name: OLEF08
Point Name: OLEF08
Point Type: L2SL
Descriptor: ELEVATOR RM
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 3 33 05
Inverted: No
Proof Point Address: 3 34 06
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: OLEF11
Point Name: OLEF11
Point Type: L2SL
Descriptor: HAZ STO AREA
Value: ON
Condition: *A3*
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: -Virtual-
Proof Point Address: 0 07 04
Normally Closed: No
Proof Delay: 10 Informational Text
Point System Name: OLEF13
Point Name: OLEF13
Point Type: L2SL
Descriptor: RM 12 CANOPY
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM09
On/Off Point Address: 3 33 06
Inverted: No
Proof Point Address: 3 34 07
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: OLEF4S
Point Name: OLEF4S
Point Type: LDI
Descriptor: EF4 SWITCH
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: OLIN.PXCM09
Point Address: 2 16 25
Normally Closed: No
Point System Name: OLEX.03.INPUT REF 1
Point Name: OLEX.03.INPUT REF 1
Point Type: LAO
Descriptor: EXF03 VFD SPEED
Value: 66.3597
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 4
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 15 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLEX.03.VFD:DAY.NIGHT
Point Name: OLEX.03.VFD:DAY.NIGHT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 15 29
Inverted: No
Point System Name: OLEX.03.VFD ALARM
Point Name: OLEX.03.VFD ALARM
Point Type: LDI
Descriptor: RUN STATUS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 0 07 05
Normally Closed: Yes
Point System Name: OLEX1E
Point Name: OLEX1E
Point Type: LAO
Descriptor: EF 1 2 4 6
Value: 1.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: K CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLEX2E
Point Name: OLEX2E
Point Type: LAO
Descriptor: EF 7 8 11 13
Value: 1.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: K CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLHTMD
Point Name: OLHTMD
Point Type: LDO
Descriptor: HEAT COOL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN .RM105:MODE
Point Name: OLIN .RM105:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.HALLWAY.ZON:MODE
Point Name: OLIN.HALLWAY.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.MBC09.TEC.COMMANDS:PPCL Address
Point Name: OLIN.MBC09.TEC.COMMANDS:PPCL Address
Point Type: LAI
Descriptor:
Value: 9
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: OLIN.OLA2.ZON:MODE
Point Name: OLIN.AHU2.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OLA3.ZON:MODE
Point Name: OLIN.OLA3.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV105.ZON:MODE
Point Name: OLIN.OV105.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV113.ZON:MODE
Point Name: OLIN.OV113.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV115.ZON:MODE
Point Name: OLIN.OV115.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV123.ZON:MODE
Point Name: OLIN.OV123.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV125.ZON:MODE
Point Name: OLIN.OV125.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV127.ZON:MODE
Point Name: OLIN.OV127.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV133.ZON:MODE
Point Name: OLIN.OV133.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV137.ZON:MODE
Point Name: OLIN.OV137.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV201.ZON:MODE
Point Name: OLIN.OV201.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV205.ZON:MODE
Point Name: OLIN.OV205.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV208.ZON:MODE
Point Name: OLIN.OV208.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV211C.ZON:MODE
Point Name: OLIN.OV211C.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV304.ZON:MODE
Point Name: OLIN.OV304.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV305.ZON:MODE
Point Name: OLIN.OV305.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV311.ZON:MODE
Point Name: OLIN.OV311.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV321.ZON:MODE
Point Name: OLIN.OV321.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV325.ZON:MODE
Point Name: OLIN.OV325.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV329.ZON:MODE
Point Name: OLIN.OV329.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV333.ZON:MODE
Point Name: OLIN.OV333.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OV339.ZON:MODE
Point Name: OLIN.OV339.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.OVENT.ZON:MODE
Point Name: OLIN.OVENT.ZON:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM101:MODE
Point Name: OLIN.RM101:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM102:MODE
Point Name: OLIN.RM102:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM103:MODE
Point Name: OLIN.RM103:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM104:MODE
Point Name: OLIN.RM104:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM106:MODE
Point Name: OLIN.RM106:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM110:MODE
Point Name: OLIN.RM110:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM112:MODE
Point Name: OLIN.RM112:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM112A:MODE
Point Name: OLIN.RM112A:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM114:MODE
Point Name: OLIN.RM114:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM116:MODE
Point Name: OLIN.RM116:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM141.ZON:MODE
Point Name: OLIN.RM141.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM142-149.ZON:MODE
Point Name: OLIN.RM142-149.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM202:MODE
Point Name: OLIN.RM202:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM204:MODE
Point Name: OLIN.RM204:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM206:MODE
Point Name: OLIN.RM206:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM210:MODE
Point Name: OLIN.RM210:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM211:MODE
Point Name: OLIN.RM211:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM211B:MODE
Point Name: OLIN.RM211B:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM219:MODE
Point Name: OLIN.RM219:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM219B:MODE
Point Name: OLIN.RM219B:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM219C:MODE
Point Name: OLIN.RM219C:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM301:MODE
Point Name: OLIN.RM301:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM302:MODE
Point Name: OLIN.RM302:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM309:MODE
Point Name: OLIN.RM309:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OLIN.RM335:MODE
Point Name: OLIN.RM335:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OV101:DAY.NGT
Point Name: OV101:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 10 29
Inverted: No
Point System Name: OV101.CTLFLMN
Point Name: OV101.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 272.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV101.ORGSTPT
Point Name: OV101.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 80.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV102:DAY.NGT
Point Name: OV102:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 09 29
Inverted: No
Point System Name: OV102.CTLFLMN
Point Name: OV102.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 332.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 09 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV102.ORGSTPT
Point Name: OV102.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV103:DAY.NGT
Point Name: OV103:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OPER
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 11 29
Inverted: No
Point System Name: OV103.CTLFLMN
Point Name: OV103.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 260.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 11 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV103.ORGSTPT
Point Name: OV103.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV104:DAY.NGT
Point Name: OV104:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 08 29
Inverted: No
Point System Name: OV104.CTLFLMN
Point Name: OV104.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 332.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 08 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV104.ORGSTPT
Point Name: OV104.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV105:DAY.NGT
Point Name: OV105:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 22 29
Inverted: No
Point System Name: OV106:DAY.NGT
Point Name: OV106:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 07 29
Inverted: No
Point System Name: OV106.CTLFLMN
Point Name: OV106.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 180.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV106.ORGSTPT
Point Name: OV106.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV109:DAY.NGT
Point Name: OV109:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 12 29
Inverted: No
Point System Name: OV109.CTLFLMN
Point Name: OV109.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 12 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV110:DAY.NGT
Point Name: OV110:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 06 29
Inverted: No
Point System Name: OV110.CTLFLMN
Point Name: OV110.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 164.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 06 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV110.ORGSTPT
Point Name: OV110.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV112E:DAY.NGT
Point Name: OV112E:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 05 29
Inverted: No
Point System Name: OV112E.CTLFLMN
Point Name: OV112E.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 176.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV112E.ORGSTPT
Point Name: OV112E.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV112I:DAY.NGT
Point Name: OV112I:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 04 29
Inverted: No
Point System Name: OV112I.CTLFLMN
Point Name: OV112I.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 52.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 04 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV112I.ORGSTPT
Point Name: OV112I.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV113:DAY.NGT
Point Name: OV113:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 13 29
Inverted: No
Point System Name: OV113.CTLFLMN
Point Name: OV113.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 160.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 13 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV113.ORGSTPT
Point Name: OV113.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV114:DAY.NGT
Point Name: OV114:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 03 29
Inverted: No
Point System Name: OV114.CTLFLMN
Point Name: OV114.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 108.0
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 03 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV114.ORGSTPT
Point Name: OV114.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV115:DAY.NGT
Point Name: OV115:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 14 29
Inverted: No
Point System Name: OV115.CTLFLMN
Point Name: OV115.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 108.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 14 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV115.ORGSTPT
Point Name: OV115.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV116:DAY.NGT
Point Name: OV116:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 02 29
Inverted: No
Point System Name: OV116.CTLFLMN
Point Name: OV116.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 332.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 02 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV116.ORGSTPT
Point Name: OV116.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV123:DAY.NGT
Point Name: OV123:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 15 29
Inverted: No
Point System Name: OV123.CTLFLMN
Point Name: OV123.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 216.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 15 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV123.ORGSTPT
Point Name: OV123.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV125:DAY.NGT
Point Name: OV125:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 16 29
Inverted: No
Point System Name: OV125.CTLFLMN
Point Name: OV125.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 16 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV125.ORGSTPT
Point Name: OV125.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV127:DAY.NGT
Point Name: OV127:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 17 29
Inverted: No
Point System Name: OV127.CTLFLMN
Point Name: OV127.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 17 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV127.ORGSTPT
Point Name: OV127.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV133:DAY.NGT
Point Name: OV133:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 18 29
Inverted: No
Point System Name: OV133.CTLFLMN
Point Name: OV133.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 160.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 18 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV133.ORGSTPT
Point Name: OV133.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV137:DAY.NGT
Point Name: OV137:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 19 29
Inverted: No
Point System Name: OV137.CTLFLMN
Point Name: OV137.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 1 19 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV137.ORGSTPT
Point Name: OV137.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV201:DAY.NGT
Point Name: OV201:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 10 29
Inverted: No
Point System Name: OV201.CTLFLMN
Point Name: OV201.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 332.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV201.ORGSTPT
Point Name: OV201.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV202:DAY.NGT
Point Name: OV202:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 12 29
Inverted: No
Point System Name: OV202.CTLFLMN
Point Name: OV202.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 260.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 12 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV202.ORGSTPT
Point Name: OV202.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV204:DAY.NGT
Point Name: OV204:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 13 29
Inverted: No
Point System Name: OV204.CTLFLMN
Point Name: OV204.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 516.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 13 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV204.ORGSTPT
Point Name: OV204.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV205:DAY.NGT
Point Name: OV205:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 11 29
Inverted: No
Point System Name: OV205.CTLFLMN
Point Name: OV205.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 80.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 11 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV205.ORGSTPT
Point Name: OV205.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV206:DAY.NGT
Point Name: OV206:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 14 29
Inverted: No
Point System Name: OV206.CTLFLMN
Point Name: OV206.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 396.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 14 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV206.ORGSTPT
Point Name: OV206.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV208:DAY.NGT
Point Name: OV208:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 15 29
Inverted: No
Point System Name: OV208.CTLFLMN
Point Name: OV208.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 15 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV208.ORGSTPT
Point Name: OV208.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV209:DAY.NGT
Point Name: OV209:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 09 29
Inverted: No
Point System Name: OV209.CTLFLMN
Point Name: OV209.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 09 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV210:DAY.NGT
Point Name: OV210:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 16 29
Inverted: No
Point System Name: OV210.CTLFLMN
Point Name: OV210.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 564.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 16 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV210.ORGSTPT
Point Name: OV210.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV211:DAY.NGT
Point Name: OV211:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 05 29
Inverted: No
Point System Name: OV211.CTLFLMN
Point Name: OV211.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 512.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV211.ORGSTPT
Point Name: OV211.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV211B:DAY.NGT
Point Name: OV211B:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 08 29
Inverted: No
Point System Name: OV211B.CTLFLMN
Point Name: OV211B.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 172.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 08 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV211B.ORGSTPT
Point Name: OV211B.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV211C:DAY.NGT
Point Name: OV211C:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 06 29
Inverted: No
Point System Name: OV211C.CTLFLMN
Point Name: OV211C.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 172.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 06 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV211C.ORGSTPT
Point Name: OV211C.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV215:DAY.NGT
Point Name: OV215:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 04 29
Inverted: No
Point System Name: OV215.CTLFLMN
Point Name: OV215.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 308.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 04 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV215.ORGSTPT
Point Name: OV215.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV219:DAY.NGT
Point Name: OV219:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 03 29
Inverted: No
Point System Name: OV219.CTLFLMN
Point Name: OV219.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 332.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 03 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV219.ORGSTPT
Point Name: OV219.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV219B:DAY.NGT
Point Name: OV219B:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 01 29
Inverted: No
Point System Name: OV219B.CTLFLMN
Point Name: OV219B.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV219B.ORGSTPT
Point Name: OV219B.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV219C:DAY.NGT
Point Name: OV219C:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 02 29
Inverted: No
Point System Name: OV219C.CTLFLMN
Point Name: OV219C.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 02 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV219C.ORGSTPT
Point Name: OV219C.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV301:DAY.NGT
Point Name: OV301:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 10 29
Inverted: No
Point System Name: OV301.CTLFLMN
Point Name: OV301.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 612.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 10 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV301.ORGSTPT
Point Name: OV301.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV302:DAY.NGT
Point Name: OV302:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 12 29
Inverted: No
Point System Name: OV302.CTLFLMN
Point Name: OV302.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 504.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 12 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV302.ORGSTPT
Point Name: OV302.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV304:DAY.NGT
Point Name: OV304:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 13 29
Inverted: No
Point System Name: OV304.CTLFLMN
Point Name: OV304.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 164.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 13 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV304.ORGSTPT
Point Name: OV304.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV305:DAY.NGT
Point Name: OV305:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 11 29
Inverted: No
Point System Name: OV305.CTLFLMN
Point Name: OV305.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 164.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 11 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV305.ORGSTPT
Point Name: OV305.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV309:DAY.NGT
Point Name: OV309:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 08 29
Inverted: No
Point System Name: OV309.CTLFLMN
Point Name: OV309.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 64.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 08 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV309.ORGSTPT
Point Name: OV309.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV311:DAY.NGT
Point Name: OV311:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 05 29
Inverted: No
Point System Name: OV311.CTLFLMN
Point Name: OV311.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 148.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV311.ORGSTPT
Point Name: OV311.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV319A:DAY.NGT
Point Name: OV319A:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 09 29
Inverted: No
Point System Name: OV319A.CTLFLMN
Point Name: OV319A.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 09 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV321:DAY.NGT
Point Name: OV321:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 07 29
Inverted: No
Point System Name: OV321.CTLFLMN
Point Name: OV321.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 216.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV321.ORGSTPT
Point Name: OV321.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV325:DAY.NGT
Point Name: OV325:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 06 29
Inverted: No
Point System Name: OV325.CTLFLMN
Point Name: OV325.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 216.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 06 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV325.ORGSTPT
Point Name: OV325.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV329:DAY.NGT
Point Name: OV329:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 03 29
Inverted: No
Point System Name: OV329.CTLFLMN
Point Name: OV329.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 160.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 03 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV329.ORGSTPT
Point Name: OV329.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV333:DAY.NGT
Point Name: OV333:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 04 29
Inverted: No
Point System Name: OV333.CTLFLMN
Point Name: OV333.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 04 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV333.ORGSTPT
Point Name: OV333.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV335:DAY.NGT
Point Name: OV335:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 01 29
Inverted: No
Point System Name: OV335.CTLFLMN
Point Name: OV335.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 92.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV335.ORGSTPT
Point Name: OV335.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV339:DAY.NGT
Point Name: OV339:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 02 29
Inverted: No
Point System Name: OV339.CTLFLMN
Point Name: OV339.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 140.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 3 02 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV339.ORGSTPT
Point Name: OV339.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV9OCC
Point Name: OV9OCC
Point Type: LDO
Descriptor: CAB 9 OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Point System Name: OVENT:DAY.NGT
Point Name: OVENT:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 07 29
Inverted: No
Point System Name: OVENT.CTLFLMN
Point Name: OVENT.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 180.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: 2 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OVENT.ORGSTPT
Point Name: OVENT.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM09
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OAECON
Point Name: OAECON
Point Type: LDO
Descriptor: ECONOMIZE MD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Point System Name: OAENTH
Point Name: OAENTH
Point Type: LAO
Descriptor: OA ENTHALPY
Value: 21.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: BTU/LB
Alarm Type: Not Alarmable
Totalization: None
Field Panel: CMC.LLMECH.RM
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OAHUMD
Point Name: OAHUMD
Point Type: LAI
Descriptor: OUT DR HUMID
Value: 46.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: CMC.LLMECH.RM
Point Address: 0 09 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.7993
COV Limit: 1.99987
Point System Name: OATEMP
Point Name: OATEMP
Point Type: LAI
Descriptor: OA TEMPERATURE
Value: 62.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: CMC.LLMECH.RM
Point Address: 0 09 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.007324
Intercept: -85.0
COV Limit: 1.0
Point System Name: O02OC
Point Name: O02OC
Point Type: LDO
Descriptor: LAB 002 TOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O04OC
Point Name: O04OC
Point Type: LDO
Descriptor: LAB 004 TOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O10OC
Point Name: O10OC
Point Type: LDO
Descriptor: LAB 010 TOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O12OC
Point Name: O12OC
Point Type: LDO
Descriptor: LAB 012 TOD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O14OC
Point Name: O14OC
Point Type: LDO
Descriptor: LAB 014 TOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O306OC
Point Name: O306OC
Point Type: LDO
Descriptor: LAB 306 TOD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O308OC
Point Name: O308OC
Point Type: LDO
Descriptor: LAB 308 TOD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O310OC
Point Name: O310OC
Point Type: LDO
Descriptor: LAB 310 TOD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: O312OC
Point Name: O312OC
Point Type: LDO
Descriptor: LAB 312 TOD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OATM08
Point Name: OATM08
Point Type: LAI
Descriptor: OAT MBC08
Value: 61.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OC02:NET OCC CMD
Point Name: OC02:NET OCC CMD
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 02 29
Inverted: No
Point System Name: OC02E
Point Name: OC02E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 1136.0
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 02 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC04:NET OCC CMD
Point Name: OC04:NET OCC CMD
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 04 29
Inverted: No
Point System Name: OC04E
Point Name: OC04E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 1936.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 04 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC08:OCC.UNOCC
Point Name: OC08:OCC.UNOCC
Point Type: LDO
Descriptor: 008 RM CTLR
Value: OCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 06 29
Inverted: No
Point System Name: OC08.ORGSTPT
Point Name: OC08.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OC08E
Point Name: OC08E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 392.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 06 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC08OV
Point Name: OC08OV
Point Type: LDI
Descriptor: RMG08 OVERRIDE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 06 24
Normally Closed: No
Point System Name: OC10:DAY.NGT
Point Name: OC10:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 07 29
Inverted: No
Point System Name: OC10.ORGSTPT
Point Name: OC10.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OC10E
Point Name: OC10E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 684.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 07 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC12:NET OCC CMD
Point Name: OC12:NET OCC CMD
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 08 29
Inverted: No
Point System Name: OC12C
Point Name: OC12C
Point Type: LDI
Descriptor: CANOPY HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 08 24
Normally Closed: No
Point System Name: OC12E
Point Name: OC12E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 2400.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 08 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC14:NET OCC CMD
Point Name: OC14:NET OCC CMD
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 17 29
Inverted: No
Point System Name: OC14E
Point Name: OC14E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 1880.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 17 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC306:NET OCC CMD
Point Name: OC306:NET OCC CMD
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 01 29
Inverted: No
Point System Name: OC306E
Point Name: OC306E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 116.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 01 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC308:NET OCC CMD
Point Name: OC308:NET OCC CMD
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 04 29
Inverted: No
Point System Name: OC308E
Point Name: OC308E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 716.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 04 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC310:NET OCC CMD
Point Name: OC310:NET OCC CMD
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 08 29
Inverted: No
Point System Name: OC310E
Point Name: OC310E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 1816.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 08 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OC312:NET OCC CMD
Point Name: OC312:NET OCC CMD
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: OVRD
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 10 29
Inverted: No
Point System Name: OC312E
Point Name: OC312E
Point Type: LAI
Descriptor: TOTAL EXH
Value: 764.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 10 53
Sensor Type: L-Type
Wire Resistance: 0.0
Slope: 4.0
Intercept: 0.0
COV Limit: 4.0
Point System Name: OH02:~OCC.UNOCC~
Point Name: OH02:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH02A
Point Name: OH02A
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH02EX
Point Name: OH02EX
Point Type: LDO
Descriptor: EXHAUST SOL
Value: ON
Condition: -N-
Priority: EMER
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 03 42
Inverted: No
Point System Name: OH02EZ
Point Name: OH02EZ
Point Type: LDI
Descriptor: EXHAUST SOL
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 03 42
Normally Closed: No
Point System Name: OH02I
Point Name: OH02I
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 03 48
Normally Closed: No
Point System Name: OH02L1
Point Name: OH02L1
Point Type: LDO
Descriptor: RELEASE CTRL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH02T
Point Name: OH02T
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH04A
Point Name: OH04A
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH04EX
Point Name: OH04EX
Point Type: LDO
Descriptor: EXHAUST SOL
Value: OFF
Condition: *F*
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 05 42
Inverted: No
Point System Name: OH04EZ
Point Name: OH04EZ
Point Type: LDI
Descriptor: EXHAUST SOL
Value: OFF
Condition: *F*
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 05 42
Normally Closed: No
Point System Name: OH04I
Point Name: OH04I
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: *F*
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 05 48
Normally Closed: No
Point System Name: OH04T
Point Name: OH04T
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH12:~OCC.UNOCC~
Point Name: OH12:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH12A
Point Name: OH12A
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: ON
Condition: *A3*
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH12I
Point Name: OH12I
Point Type: LDI
Descriptor: HOOD START
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 12 48
Normally Closed: No
Point System Name: OH12T
Point Name: OH12T
Point Type: LAO
Descriptor: HOOD TIMER
Value: 33835.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH14A:~OCC.UNOCC~
Point Name: OH14A:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14AA
Point Name: OH14AA
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14AI
Point Name: OH14AI
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 14 48
Normally Closed: No
Point System Name: OH14AT
Point Name: OH14AT
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH14B:~OCC.UNOCC~
Point Name: OH14B:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14BA
Point Name: OH14BA
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14BI
Point Name: OH14BI
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 16 48
Normally Closed: No
Point System Name: OH14BT
Point Name: OH14BT
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH14C:~OCC.UNOCC~
Point Name: OH14C:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14CA
Point Name: OH14CA
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14CI
Point Name: OH14CI
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 18 48
Normally Closed: No
Point System Name: OH14CT
Point Name: OH14CT
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH14D:~OCC.UNOCC~
Point Name: OH14D:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14DA
Point Name: OH14DA
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH14DI
Point Name: OH14DI
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 20 48
Normally Closed: No
Point System Name: OH14DT
Point Name: OH14DT
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH306:~OCC.UNOCC~
Point Name: OH306:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH306A
Point Name: OH306A
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH306I
Point Name: OH306I
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 02 48
Normally Closed: No
Point System Name: OH306T
Point Name: OH306T
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH308:~OCC.UNOCC~
Point Name: OH308:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH308A
Point Name: OH308A
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH308I
Point Name: OH308I
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 05 48
Normally Closed: No
Point System Name: OH308T
Point Name: OH308T
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH310:~OCC.UNOCC~
Point Name: OH310:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH310A
Point Name: OH310A
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH310I
Point Name: OH310I
Point Type: LDI
Descriptor: HOOD START
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 07 48
Normally Closed: No
Point System Name: OH310T
Point Name: OH310T
Point Type: LAO
Descriptor: HOOD TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OH312:~OCC.UNOCC~
Point Name: OH312:~OCC.UNOCC~
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH312A
Point Name: OH312A
Point Type: LDO
Descriptor: HOOD TIMEOUT
Value: ON
Condition: *A3*
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OH312I
Point Name: OH312I
Point Type: LDI
Descriptor: HOOD START
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 11 48
Normally Closed: No
Point System Name: OH312T
Point Name: OH312T
Point Type: LAO
Descriptor: HOOD TIMER
Value: 145159.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MIN
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL.HEAD.HOUSE1.ZON:MODE
Point Name: OL.HEAD.HOUSE1.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OL.HEAD.HOUSE2.ZON:MODE
Point Name: OL.HEAD.HOUSE2.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OL.PNL08.SHEDTMR
Point Name: OL.PNL08.SHEDTMR
Point Type: LAO
Descriptor: MBC08 SHED TIMER
Value: 67108864.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL14NO
Point Name: OL14NO
Point Type: LDI
Descriptor: NGT OVRD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 17 19
Normally Closed: No
Point System Name: OL14OR
Point Name: OL14OR
Point Type: LDI
Descriptor: OVER RIDE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OL306NO
Point Name: OL306NO
Point Type: LDI
Descriptor: NGT OVRD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 01 19
Normally Closed: No
Point System Name: OL306OR
Point Name: OL306OR
Point Type: LDI
Descriptor: OVER RIDE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OL308NO
Point Name: OL308NO
Point Type: LDI
Descriptor: NGT OVRD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 04 19
Normally Closed: No
Point System Name: OL308OR
Point Name: OL308OR
Point Type: LDI
Descriptor: OVER RIDE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OL310NO
Point Name: OL310NO
Point Type: LDI
Descriptor: NGT OVRD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 08 19
Normally Closed: No
Point System Name: OL310OR
Point Name: OL310OR
Point Type: LDI
Descriptor: OVER RIDE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OL312NO
Point Name: OL312NO
Point Type: LDI
Descriptor: NGT OVRD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 10 19
Normally Closed: No
Point System Name: OL312OR
Point Name: OL312OR
Point Type: LDI
Descriptor: OVER RIDE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLA1.FAN.DP.SW
Point Name: OLA1.FANDP.SW
Point Type: LDI
Descriptor: FAN DP SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 16
Normally Closed: No
Point System Name: OLA1.SAFETY
Point Name: OLA1.SAFETY
Point Type: LDO
Descriptor: SAFETY SHUTDOWN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 06 04
Inverted: Yes
Point System Name: OLA1.VFD:DAY.NIGHT
Point Name: OLA1.VFD:DAY.NIGHT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 31 29
Inverted: No
Point System Name: OLA1AM
Point Name: OLA1AM
Point Type: LAO
Descriptor: ACTUAL OFSET
Value: 25.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: K CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OLA1BI
Point Name: OLA1BI
Point Type: LAO
Descriptor: LOOP BIAS
Value: 11.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UNITS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1BP
Point Name: OLA1BP
Point Type: LDI
Descriptor: VFD BYPASS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 06
Normally Closed: No
Point System Name: OLA1CM
Point Name: OLA1CM
Point Type: LAO
Descriptor: MAX CLG VLV
Value: 14.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1CV
Point Name: OLA1CV
Point Type: LAO
Descriptor: COOL VALVE
Value: 11.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 02 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.19986
Point System Name: OLA1DA
Point Name: OLA1DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 54.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 50.0
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008139
Intercept: -50.00141
COV Limit: 1.00006
Point System Name: OLA1DC
Point Name: OLA1DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 16.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLA1DH
Point Name: OLA1DH
Point Type: LAI
Descriptor: DIS AIR HUMD
Value: 19.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 0.99994
Point System Name: OLA1DP
Point Name: OLA1DP
Point Type: LAI
Descriptor: DA DUCT SP
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 2.0
Low Limit: 0.5
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24912
COV Limit: 0.10003
Point System Name: OLA1DS
Point Name: OLA1DS
Point Type: LAO
Descriptor: STATIC SET
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
Point System Name: OLA1EM
Point Name: OLA1EM
Point Type: LDO
Descriptor: ECONO MODE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLA1FF
Point Name: OLA1FF
Point Type: LDI
Descriptor: BAG FLTR ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 09
Normally Closed: Yes
Point System Name: OLA1FL
Point Name: OLA1FL
Point Type: LDI
Descriptor: VFD FAILURE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 05
Normally Closed: No
Point System Name: OLA1FZ
Point Name: OLA1FZ
Point Type: LDI
Descriptor: FREEZE STAT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 07
Normally Closed: No
Point System Name: OLA1HC
Point Name: OLA1HC
Point Type: LAO
Descriptor: DIS HUM SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1HM
Point Name: OLA1HM
Point Type: LAO
Descriptor: HUMIDIFIER
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 02 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.19986
Point System Name: OLA1HP
Point Name: OLA1HP
Point Type: LAO
Descriptor: HUMID RESET
Value: 20.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1HS
Point Name: OLA1HS
Point Type: LDO
Descriptor: HIGH STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLA1HT
Point Name: OLA1HT
Point Type: LAI
Descriptor: HEAT TEMP
Value: 71.46
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 40.0
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008139
Intercept: -50.00141
COV Limit: 1.00006
Point System Name: OLA1HV
Point Name: OLA1HV
Point Type: LAO
Descriptor: HEAT VALVE
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.19986
Point System Name: OLA1LI
Point Name: OLA1LI
Point Type: LAO
Descriptor: LOOP INPUT
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H20
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09991
Point System Name: OLA1LO
Point Name: OLA1LO
Point Type: LAO
Descriptor: LOOP OUTPUT
Value: 77.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1MC
Point Name: OLA1MC
Point Type: LAO
Descriptor: MIX DPR CTRL
Value: 16.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1MO
Point Name: OLA1MO
Point Type: LAO
Descriptor: OUT AIR MIN
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1MS
Point Name: OLA1MS
Point Type: LAO
Descriptor: MIXED AIR STPT
Value: 50.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.25
Point System Name: OLA1MT
Point Name: OLA1MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 65.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 0.0
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008139
Intercept: -50.00141
COV Limit: 1.00006
Point System Name: OLA1P1
Point Name: OLA1P1
Point Type: LAI
Descriptor: RA AFMS DP
Value: -16.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UINH2O
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.04069
Intercept: -249.99858
COV Limit: 1.01561
Point System Name: OLA1P2
Point Name: OLA1P2
Point Type: LAI
Descriptor: RA AFMS DP
Value: -11.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UINH2O
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.04069
Intercept: -249.99858
COV Limit: 1.01561
Point System Name: OLA1P3
Point Name: OLA1P3
Point Type: LAI
Descriptor: DA AFMS DP
Value: 40.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UINH2O
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.04069
Intercept: -249.99858
COV Limit: 1.01561
Point System Name: OLA1PF
Point Name: OLA1PF
Point Type: LDI
Descriptor: PRE FLTR ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 08
Normally Closed: Yes
Point System Name: OLA1PM
Point Name: OLA1PM
Point Type: LAO
Descriptor: PREHEAT MIN
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1PS
Point Name: OLA1PS
Point Type: LAO
Descriptor: PREHEAT STPT
Value: 51.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1PT
Point Name: OLA1PT
Point Type: LAI
Descriptor: PREHEAT TEMP
Value: 67.71
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 100.0
Low Limit: 31.99
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008141
Intercept: -50.00704
COV Limit: 1.00032
Point System Name: OLA1PV
Point Name: OLA1PV
Point Type: LAO
Descriptor: PREHEAT VALV
Value: 12.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.19986
Point System Name: OLA1R1
Point Name: OLA1R1
Point Type: LAO
Descriptor: RET 1 VOL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLA1R2
Point Name: OLA1R2
Point Type: LAO
Descriptor: RET 2 VOL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLA1RP
Point Name: OLA1RP
Point Type: LAI
Descriptor: RET DUCT PSR
Value: -70.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UINH2O
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.08138
Intercept: -1500.0
COV Limit: 30.0
Point System Name: OLA1RV
Point Name: OLA1RV
Point Type: LAO
Descriptor: RETURN VOL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 400.0
Point System Name: OLA1SC
Point Name: OLA1SC
Point Type: LAO
Descriptor: SUPLY SETPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLA1SH
Point Name: OLA1SH
Point Type: LAI
Descriptor: RM 115 HUMD
Value: 26.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -18.9993
COV Limit: 0.99994
Point System Name: OLA1SS
Point Name: OLA1SS
Point Type: L2SL
Descriptor: AHU 1 SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM08
On/Off Point Address: 2 31 24
Inverted: No
Proof Point Address: 2 31 23
Normally Closed: No
Proof Delay: 300 Informational Text
Point System Name: OLA1SV
Point Name: OLA1SV
Point Type: LAO
Descriptor: SUPPLY VOL
Value: 25251.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 400.0
Point System Name: OLA1TM
Point Name: OLA1TM
Point Type: LAO
Descriptor: TRACK SETPT
Value: 17.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: K CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OLBLDE
Point Name: OLBLDE
Point Type: LAO
Descriptor: TOT BLD EXH
Value: 16.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: K CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 200.0
Point System Name: OLCHWH
Point Name: OLCHWH
Point Type: LAI
Descriptor: CHW FLOW MTR
Value: 91.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 09 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.08138
Intercept: -500.0
COV Limit: 25.0
Point System Name: OLCHWR
Point Name: OLCHWR
Point Type: LAI
Descriptor: CHWR TEMP
Value: 56.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.996
Point System Name: OLCHWS
Point Name: OLCHWS
Point Type: LAI
Descriptor: CHWS TEMP
Value: 46.47
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 60.01
Low Limit: 40.01
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.996
Point System Name: OLCNTA
Point Name: OLCNTA
Point Type: LDI
Descriptor: CONTROL AIR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 11
Normally Closed: No
Point System Name: OLCONM
Point Name: OLCONM
Point Type: LPACI
Descriptor: CONDENSATE
Value: 28830.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: LB HR
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 07
Gain: 100.0
Count Both Edges: No
COV Limit: 10000.0
Point System Name: OLDC1
Point Name: OLDC1
Point Type: LDI
Descriptor: DUST COLLECT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: OLIN.PXCM08
Point Address: 0 05 10
Normally Closed: No
Point System Name: OLDHWC
Point Name: OLDHWC
Point Type: LAO
Descriptor: DOM HW SET
Value: 130.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.99988
Point System Name: OLDHWT
Point Name: OLDHWT
Point Type: LAI
Descriptor: DOM HOT TMP
Value: 130.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 139.99
Low Limit: 79.99
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 04 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008952
Intercept: -25.00014
COV Limit: 0.996
Point System Name: OLDHWV
Point Name: OLDHWV
Point Type: LAO
Descriptor: DOM HW VLV
Value: 6.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 02 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
Point System Name: OLDI1A
Point Name: OLDI1A
Point Type: LDO
Descriptor: DI PUMP1 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLDI2A
Point Name: OLDI2A
Point Type: LDO
Descriptor: DI PUMP2 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLDILD
Point Name: OLDILD
Point Type: LAO
Descriptor: PUMP LEAD
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PUMP
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLDIP1
Point Name: OLDIP1
Point Type: L2SL
Descriptor: DI PUMP 1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM08
On/Off Point Address: 0 06 05
Inverted: Yes
Proof Point Address: 0 11 01
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: OLDIP2
Point Name: OLDIP2
Point Type: L2SL
Descriptor: DI PUMP 2
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM08
On/Off Point Address: 0 06 06
Inverted: Yes
Proof Point Address: 0 11 02
Normally Closed: No
Proof Delay: 30 Informational Text
Point System Name: OLDIWT
Point Name: OLDIWT
Point Type: LDI
Descriptor: DI WATER
Value: ON
Condition: *A3*
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 01
Normally Closed: No
Point System Name: OLDMUSIC.COND
Point Name: OLDMUSIC.COND
Point Type: LPACI
Descriptor: MUSIC COND MTR
Value: 335980.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 11 06
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
Point System Name: OLEMTS
Point Name: OLEMTS
Point Type: LDI
Descriptor: OL EMER TS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 13
Normally Closed: No
Point System Name: OLEXHT
Point Name: OLEXHT
Point Type: LAO
Descriptor: EXH FAN TOT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: K CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 200.0
Point System Name: OLFIRE
Point Name: OLFIRE
Point Type: LDI
Descriptor: FIRE ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 14
Normally Closed: No
Point System Name: OLHD.FC01.CCV
Point Name: OLHD.FC01.CCV
Point Type: LAO
Descriptor: CHW VALVE
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 01 05
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.25
Point System Name: OLHD.FC01.DAY.RHS
Point Name: OLHD.FC01.DAY.RHS
Point Type: LAO
Descriptor: DAY RH SETPT
Value: 60.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC01.DAY.RMS
Point Name: OLHD.FC01.DAY.RMS
Point Type: LAO
Descriptor: DAY RMT SETPT
Value: 68.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC01.EH1
Point Name: OLHD.FC01.EH1
Point Type: LDO
Descriptor: ELEC HT STAGE 1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 07 02
Inverted: No
Point System Name: OLHD.FC01.EH2
Point Name: OLHD.FC01.EH2
Point Type: LDO
Descriptor: ELEC HT STAGE 2
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 07 03
Inverted: No
Point System Name: OLHD.FC01.EH3
Point Name: OLHD.FC01.EH3
Point Type: LDO
Descriptor: ELEC HT STAGE 3
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 08 01
Inverted: No
Point System Name: OLHD.FC01.HME
Point Name: OLHD.FC01.HME
Point Type: LDO
Descriptor: FAN COIL 1 HUMD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 08 02
Inverted: No
Point System Name: OLHD.FC01.LOOPOUT
Point Name: OLHD.FC01.LOOPOUT
Point Type: LAO
Descriptor: SAT LOOPOUT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC01.NGT.RHS
Point Name: OLHD.FC01.NGT.RHS
Point Type: LAO
Descriptor: NGT RH SETPT
Value: 60.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC01.NGT.RMS
Point Name: OLHD.FC01.NGT.RMS
Point Type: LAO
Descriptor: NGT RMT SETPT
Value: 68.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC01.OCC
Point Name: OLHD.FC01.OCC
Point Type: LDO
Descriptor: FAN COIL 1 OCC
Value: OFF
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLHD.FC01.RAH
Point Name: OLHD.FC01.RAH
Point Type: LAI
Descriptor: RETURN AIR RH
Value: 69.76
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.00014
COV Limit: 2.0
Point System Name: OLHD.FC01.RAT
Point Name: OLHD.FC01.RAT
Point Type: LAI
Descriptor: RETURN AIR TEMP
Value: 68.31
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 85.0
Low Limit: 55.0
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -5.00014
COV Limit: 0.5
Point System Name: OLHD.FC01.RHS
Point Name: OLHD.FC01.RHS
Point Type: LAO
Descriptor: RH SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC01.RMS
Point Name: OLHD.FC01.RMS
Point Type: LAO
Descriptor: RMT SETPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC01.SAS
Point Name: OLHD.FC01.SAS
Point Type: LAO
Descriptor: SUPPLY AIR STPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.25
Point System Name: OLHD.FC01.SAT
Point Name: OLHD.FC01.SAT
Point Type: LAI
Descriptor: SUPPLY AIR TEMP
Value: 68.55
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -5.00014
COV Limit: 0.5
Point System Name: OLHD.FC01.SS
Point Name: OLHD.FC01.SS
Point Type: L2SL
Descriptor: SUPPLY FAN
Value: OFF
Condition: -N-
Priority: OPER
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
On/Off Point Address: 0 07 01
Inverted: No
Proof Point Address: 0 04 05
Normally Closed: No
Proof Delay: 15 Informational Text
Point System Name: OLHD.FC02.CCV
Point Name: OLHD.FC02.CCV
Point Type: LAO
Descriptor: CHW VALVE
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VDC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 01 06
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.25
Point System Name: OLHD.FC02.DAY.RHS
Point Name: OLHD.FC02.DAY.RHS
Point Type: LAO
Descriptor: DAY RH SETPT
Value: 60.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC02.DAY.RMS
Point Name: OLHD.FC02.DAY.RMS
Point Type: LAO
Descriptor: DAY RMT SETPT
Value: 68.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC02.EH1
Point Name: OLHD.FC02.EH1
Point Type: LDO
Descriptor: ELEC HT STAGE 1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 07 05
Inverted: No
Point System Name: OLHD.FC02.EH2
Point Name: OLHD.FC02.EH2
Point Type: LDO
Descriptor: ELEC HT STAGE 2
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 07 06
Inverted: No
Point System Name: OLHD.FC02.EH3
Point Name: OLHD.FC02.EH3
Point Type: LDO
Descriptor: ELEC HT STAGE 3
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 08 04
Inverted: No
Point System Name: OLHD.FC02.HME
Point Name: OLHD.FC02.HME
Point Type: LDO
Descriptor: FAN COIL 2 HUMD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 08 05
Inverted: No
Point System Name: OLHD.FC02.LOOPOUT
Point Name: OLHD.FC02.LOOPOUT
Point Type: LAO
Descriptor: SAT LOOPOUT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC02.NGT.RHS
Point Name: OLHD.FC02.NGT.RHS
Point Type: LAO
Descriptor: NGT RH SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC02.NGT.RMS
Point Name: OLHD.FC02.NGT.RMS
Point Type: LAO
Descriptor: NGT RMT SETPT
Value: 68.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC02.OCC
Point Name: OLHD.FC02.OCC
Point Type: LDO
Descriptor: FAN COIL 2 OCC
Value: OFF
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLHD.FC02.RAH
Point Name: OLHD.FC02.RAH
Point Type: LAI
Descriptor: RETURN AIR RH
Value: 68.32
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.0
COV Limit: 2.0
Point System Name: OLHD.FC02.RAT
Point Name: OLHD.FC02.RAT
Point Type: LAI
Descriptor: RETURN AIR TEMP
Value: 127.35
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 85.0
Low Limit: 55.0
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -5.00014
COV Limit: 0.5
Point System Name: OLHD.FC02.RHS
Point Name: OLHD.FC02.RHS
Point Type: LAO
Descriptor: RH SETPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC02.RMS
Point Name: OLHD.FC02.RMS
Point Type: LAO
Descriptor: RMT SETPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLHD.FC02.SAS
Point Name: OLHD.FC02.SAS
Point Type: LAO
Descriptor: SUPPLY AIR STPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.25
Point System Name: OLHD.FC02.SAT
Point Name: OLHD.FC02.SAT
Point Type: LAI
Descriptor: SUPPLY AIR TEMP
Value: 86.99
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -5.00014
COV Limit: 0.5
Point System Name: OLHD.FC02.SS
Point Name: OLHD.FC02.SS
Point Type: L2SL
Descriptor: SUPPLY FAN
Value: OFF
Condition: -N-
Priority: OPER
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
On/Off Point Address: 0 07 04
Inverted: No
Proof Point Address: 0 04 06
Normally Closed: No
Proof Delay: 15 Informational Text
Point System Name: OLHWCV
Point Name: OLHWCV
Point Type: LAO
Descriptor: CONVRT VALVE
Value: 11.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.19986
Point System Name: OLHWP1
Point Name: OLHWP1
Point Type: L2SL
Descriptor: RAD PUMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM08
On/Off Point Address: 0 06 01
Inverted: Yes
Proof Point Address: 0 05 02
Normally Closed: No
Proof Delay: 15 Informational Text
Point System Name: OLHWP3
Point Name: OLHWP3
Point Type: L2SL
Descriptor: AHU PUMP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM08
On/Off Point Address: 0 06 02
Inverted: Yes
Proof Point Address: 0 05 03
Normally Closed: No
Proof Delay: 15 Informational Text
Point System Name: OLHWP4
Point Name: OLHWP4
Point Type: L2SL
Descriptor: REHEAT PUMP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: OLIN.PXCM08
On/Off Point Address: 0 06 03
Inverted: Yes
Proof Point Address: 0 05 04
Normally Closed: No
Proof Delay: 15 Informational Text
Point System Name: OLHWRT
Point Name: OLHWRT
Point Type: LAI
Descriptor: HWR TEMP
Value: 118.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 200.0
Low Limit: 80.01
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.996
Point System Name: OLHWSC
Point Name: OLHWSC
Point Type: LAO
Descriptor: HOTWTR RESET
Value: 120.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.99687
Point System Name: OLHWST
Point Name: OLHWST
Point Type: LAI
Descriptor: HWS TEMP
Value: 119.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 200.0
Low Limit: 80.01
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 03 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.996
Point System Name: OLIN.COND
Point Name: OLIN.COND
Point Type: LPACI
Descriptor: OLIN CONDENSATE
Value: 1349950.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 11 07
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
Point System Name: OLIN.COND.METER
Point Name: OLIN.COND.METER
Point Type: LPACI
Descriptor: OLIN CONDENSATE
Value: 1349950.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 11 07
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
Point System Name: OLIN.E.TEST
Point Name: OLIN.E.TEST
Point Type: LPACI
Descriptor:
Value: 2297732.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 08
Gain: 1.6
Count Both Edges: No
COV Limit: 1.6
Point System Name: OLIN.ELEC
Point Name: OLIN.ELEC
Point Type: LPACI
Descriptor: LPACI
Value: 266217.4063
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: WH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 10 08
Gain: 1.6
Count Both Edges: No
COV Limit: 1.6
Point System Name: OLIN.ELEC.DEMAND
Point Name: OLIN.ELEC.DEMAND
Point Type: LAO
Descriptor: ELECTRIC DEMAND
Value: 56.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.ELEC.METER.READING
Point Name: OLIN.ELEC.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 266217.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OLIN.ELECTRIC:PPCL Address
Point Name: OLIN.ELECTRIC:PPCL Address
Point Type: LAI
Descriptor:
Value: 8
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: OLIN.H2O.METER.READING
Point Name: OLIN.H2O.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 9100806
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OLIN.HIGH.H2O:PPCL Address
Point Name: OLIN.HIGH.H2O:PPCL Address
Point Type: LAI
Descriptor:
Value: 8
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: OLIN.LAST.MONTH.ELEC.CONSUMP
Point Name: OLIN.LAST.MONTH.ELEC.CONSUMP
Point Type: LAO
Descriptor: LAST MNTH CONSMP
Value: 38083.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.LAST.MONTH.H2O.CONSUMP
Point Name: OLIN.LAST.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST MNTH CONSMP
Value: 21084
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.LAST.MONTH.STEAM.CONSU
Point Name: OLIN.LAST.MONTH.STEAM.CONSU
Point Type: LAO
Descriptor: LAST MONTH STEAM
Value: 4032.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLIN.LAST.WEEK.ELEC.CONSUMP
Point Name: OLIN.LAST.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 9796.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.LAST.WEEK.H2O.CONSUMP
Point Name: OLIN.LAST.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 6946
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.LAST.WEEK.STEAM.CONSU
Point Name: OLIN.LAST.WEEK.STEAM.CONSU
Point Type: LAO
Descriptor: LAST WEEK STEAM
Value: 1096.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLIN.LOW.H2O:PPCL Address
Point Name: OLIN.LOW.H2O:PPCL Address
Point Type: LAI
Descriptor:
Value: 8
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: OLIN.MBC08.TEC.COMMANDS:PPCL Address
Point Name: OLIN.MBC08.TEC.COMMANDS:PPCL Address
Point Type: LAI
Descriptor:
Value: 8
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: OLIN.MONTH.ELEC.CONSUMP
Point Name: OLIN.MONTH.ELEC.CONSUMP
Point Type: LAO
Descriptor: THIS MNTH CONSMP
Value: 20510.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.MONTH.H2O.CONSUMP
Point Name: OLIN.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: THIS MNTH CONSMP
Value: 13465
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.MONTH.STEAM.CONSUMP
Point Name: OLIN.MONTH.STEAM.CONSUMP
Point Type: LAO
Descriptor: MONTH STEAM
Value: 2170.68
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLIN.OAT
Point Name: OLIN.OAT
Point Type: LAO
Descriptor: VIRT OA TEMP
Value: 61.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.OV18A.ZON:MODE
Point Name: OLIN.OV18A.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.OVHED.ZON:MODE
Point Name: OLIN.OVHED.ZON:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM002:MODE
Point Name: OLIN.RM002:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM004:MODE
Point Name: OLIN.RM004:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM007:MODE
Point Name: OLIN.RM007:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM007A:MODE
Point Name: OLIN.RM007A:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM011:MODE
Point Name: OLIN.RM011:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM012:MODE
Point Name: OLIN.RM012:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM014:MODE
Point Name: OLIN.RM014:MODE
Point Type: LENUM
Descriptor:
Value: VAC
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM015:MODE
Point Name: OLIN.RM015:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM019:MODE
Point Name: OLIN.RM019:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM08:MODE
Point Name: OLIN.RM08:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM306:MODE
Point Name: OLIN.RM306:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM308:MODE
Point Name: OLIN.RM308:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM310:MODE
Point Name: OLIN.RM310:MODE
Point Type: LENUM
Descriptor:
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.RM312:MODE
Point Name: OLIN.RM312:MODE
Point Type: LENUM
Descriptor: Mode Output
Value: OCC1
Condition: -N-
Priority: NONE
Text Table: ZONE_MODE
0 - VAC
1 - OCC1
2 - OCC2
3 - OCC3
4 - OCC4
5 - OCC5
6 - WARMUP
7 - COOLDOWN
8 - NGHT_HTG
9 - NGHT_CLG
10 - STOP_HTG
11 - STOP_CLG
Alarm Type: Not Alarmable
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLIN.STEAM:PPCL Address
Point Name: OLIN.STEAM:PPCL Address
Point Type: LAI
Descriptor:
Value: 8
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
Point System Name: OLIN.STEAM.DEMAND
Point Name: OLIN.STEAM.DEMAND
Point Type: LAI
Descriptor: STEAM DEMAND
Value: 5.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM/HR
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: OLIN.PXCM08
Point Address: 0 04 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.730265
Intercept: -4486.75
COV Limit: 50.0
Point System Name: OLIN.TODAY.ELEC.CONSUMP
Point Name: OLIN.TODAY.ELEC.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 864.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.TODAY.H2O.CONSUMP
Point Name: OLIN.TODAY.H2O.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 326
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.TODAY.STEAM.CONSUMP
Point Name: OLIN.TODAY.STEAM.CONSUMP
Point Type: LAO
Descriptor: TODAY STEAM
Value: 9.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLIN.TUNNEL
Point Name: OLIN.TUNNEL
Point Type: LDI
Descriptor: DOOR ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 15
Normally Closed: Yes
Point System Name: OLIN.WATER.DEMAND
Point Name: OLIN.WATER.DEMAND
Point Type: LAO
Descriptor: OLIN H2O DEMAND
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.WATER.HI
Point Name: OLIN.WATER.HI
Point Type: LPACI
Descriptor: LPACI
Value: 8285870.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 04 03
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
Point System Name: OLIN.WATER.HIGH
Point Name: OLIN.WATER.HIGH
Point Type: LAO
Descriptor: PDL WATER HIGH
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.WATER.LO
Point Name: OLIN.WATER.LO
Point Type: LPACI
Descriptor: LPACI
Value: 814937.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 04 04
Gain: 1.0
Count Both Edges: No
COV Limit: 1.0
Point System Name: OLIN.WATER.LOW
Point Name: OLIN.WATER.LOW
Point Type: LAO
Descriptor: PDL WATER LOW
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.WEEK.ELEC.CONSUMP
Point Name: OLIN.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.WEEK.H2O.CONSUMP
Point Name: OLIN.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.WEEK.STEAM.CONSUMP
Point Name: OLIN.WEEK.STEAM.CONSUMP
Point Type: LAO
Descriptor: WEEK STEAM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLIN.YEST.ELEC.CONSUMP
Point Name: OLIN.YEST.ELEC.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 1092.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.YEST.H2O.CONSUMP
Point Name: OLIN.YEST.H2O.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 112
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.YEST.STEAM.CONSUMP
Point Name: OLIN.YEST.STEAM.CONSUMP
Point Type: LAO
Descriptor: YEST STEAM
Value: 134.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
Point System Name: OLLABE
Point Name: OLLABE
Point Type: LAO
Descriptor: TOT LAB EXH
Value: 11.81
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: K CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 200.0
Point System Name: OLOCC
Point Name: OLOCC
Point Type: LDO
Descriptor: OLIN OCC PNT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OLSEP1
Point Name: OLSEP1
Point Type: LDI
Descriptor: SEWAGE PMP 1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 0 05 12
Normally Closed: No
Point System Name: OLSEP2
Point Name: OLSEP2
Point Type: LDI
Descriptor: SEWAGE PMP 2
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 22 24
Normally Closed: No
Point System Name: OM12:OCC UNOCC
Point Name: OM12:OCC UNOCC
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 11 29
Inverted: No
Point System Name: OM12A
Point Name: OM12A
Point Type: LDI
Descriptor: HD 12 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 11 07
Normally Closed: No
Point System Name: OM14A:OCC UNOCC
Point Name: OM14A:OCC UNOCC
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 13 29
Inverted: No
Point System Name: OM14AA
Point Name: OM14AA
Point Type: LDI
Descriptor: HD 14A ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 13 07
Normally Closed: No
Point System Name: OM14B:OCC UNOCC
Point Name: OM14B:OCC UNOCC
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 15 29
Inverted: No
Point System Name: OM14BA
Point Name: OM14BA
Point Type: LDI
Descriptor: HD 14B ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 15 07
Normally Closed: No
Point System Name: OM14D:OCC UNOCC
Point Name: OM14D:OCC UNOCC
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 21 29
Inverted: No
Point System Name: OM14DA
Point Name: OM14DA
Point Type: LDI
Descriptor: HD 14D ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 21 07
Normally Closed: No
Point System Name: OM306:OCC UNOCC
Point Name: OM306:OCC UNOCC
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 03 29
Inverted: No
Point System Name: OM306A
Point Name: OM306A
Point Type: LDI
Descriptor: HD 306 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 03 07
Normally Closed: No
Point System Name: OM308:OCC UNOCC
Point Name: OM308:OCC UNOCC
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 06 29
Inverted: No
Point System Name: OM308A
Point Name: OM308A
Point Type: LDI
Descriptor: HD 308 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 06 07
Normally Closed: No
Point System Name: OM310:OCC UNOCC
Point Name: OM310:OCC UNOCC
Point Type: LDO
Descriptor:
Value: UNOCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 09 29
Inverted: No
Point System Name: OM310A
Point Name: OM310A
Point Type: LDI
Descriptor: HD 310 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 09 07
Normally Closed: No
Point System Name: OM312:OCC UNOCC
Point Name: OM312:OCC UNOCC
Point Type: LDO
Descriptor:
Value: OCC
Condition: -N-
Priority: NONE
Text Table: OCC_UNOCC
0 - OCC
1 - UNOCC
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 12 29
Inverted: No
Point System Name: OM312A
Point Name: OM312A
Point Type: LDI
Descriptor: HD 312 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 3 12 07
Normally Closed: No
Point System Name: OV003:DAY.NGT
Point Name: OV003:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 01 29
Inverted: No
Point System Name: OV003.CTLFLMN
Point Name: OV003.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 160.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV007:DAY.NGT
Point Name: OV007:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 03 29
Inverted: No
Point System Name: OV007.CTLFLMN
Point Name: OV007.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 456.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 03 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV007.ORGSTPT
Point Name: OV007.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV007A:DAY.NGT
Point Name: OV007A:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 02 29
Inverted: No
Point System Name: OV007A.CTLFLMN
Point Name: OV007A.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 84.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 02 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV007A.ORGSTPT
Point Name: OV007A.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV008:DAY.NGT
Point Name: OV008:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 23 29
Inverted: No
Point System Name: OV008A:DAY.NGT
Point Name: OV008A:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 24 29
Inverted: No
Point System Name: OV011:DAY.NGT
Point Name: OV011:DAY.NGT
Point Type: LDO
Descriptor:
Value: NIGHT
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 04 29
Inverted: No
Point System Name: OV011.CTLFLMN
Point Name: OV011.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 704.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 04 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV011.ORGSTPT
Point Name: OV011.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV013:DAY.NGT
Point Name: OV013:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 08 29
Inverted: No
Point System Name: OV015:DAY.NGT
Point Name: OV015:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 05 29
Inverted: No
Point System Name: OV015.CTLFLMN
Point Name: OV015.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 148.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 05 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV015.ORGSTPT
Point Name: OV015.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV017:DAY.NGT
Point Name: OV017:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 06 29
Inverted: No
Point System Name: OV017.CTLFLMN
Point Name: OV017.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 164.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 06 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV017.ORGSTPT
Point Name: OV017.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV019:DAY.NGT
Point Name: OV019:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 07 29
Inverted: No
Point System Name: OV019.CTLFLMN
Point Name: OV019.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 2 07 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV019.ORGSTPT
Point Name: OV019.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OV18A:DAY.NGT
Point Name: OV18A:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 22 29
Inverted: No
Point System Name: OV18A.CTLFLMN
Point Name: OV18A.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 520.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 22 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OV18A.ORGSTPT
Point Name: OV18A.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OVBY20
Point Name: OVBY20
Point Type: LDO
Descriptor: VAV BYPASS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OVBY23
Point Name: OVBY23
Point Type: LDO
Descriptor: VAV BYPASS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OVHED:DAY.NGT
Point Name: OVHED:DAY.NGT
Point Type: LDO
Descriptor:
Value: DAY
Condition: -N-
Priority: OVRD
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 01 29
Inverted: No
Point System Name: OVHED.CTLFLMN
Point Name: OVHED.CTLFLMN
Point Type: LAO
Descriptor: MIN FLOW SETPT
Value: 180.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: 1 01 76
Actuator Type Voltage
Slope: 4.0
Intercept: 0.0
COV Limit: 10.0
Point System Name: OVHED.ORGSTPT
Point Name: OVHED.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OVRS20
Point Name: OVRS20
Point Type: LDO
Descriptor: VAV RESET
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OVRS23
Point Name: OVRS23
Point Type: LDO
Descriptor: VAV RESET
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.PXCM08
Point Address: -Virtual-
Point System Name: OL.OLFCU.CCO
Point Name: OL.OLFCU.CCO
Point Type: LAO
Descriptor: COOLING COIL OUT
Value: 12.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL.OLFCU.CCV
Point Name: OL.OLFCU.CCV
Point Type: LAO
Descriptor: COILIN VLV
Value: 1.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: V
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: 0 00 09
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.2
Point System Name: OL.OLFCU.FAN
Point Name: OL.OLFCU.FAN
Point Type: LAO
Descriptor: FAN SPEED
Value: 5.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 1
Engineering Units: VOLTS
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: 0 00 10
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.1
Point System Name: OL.OLFCU.FAN.STPT
Point Name: OL.OLFCU.FAN.STPT
Point Type: LAO
Descriptor: SPEED STPT
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL.OLFCU.OCC
Point Name: OL.OLFCU.OCC
Point Type: LDO
Descriptor: OCC / UNOCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: -Virtual-
Point System Name: OL.OLFCU.RMS
Point Name: OL.OLFCU.RMS
Point Type: LAO
Descriptor: SUPPLY STPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL.OLFCU.RMT
Point Name: OL.OLFCU.RMT
Point Type: LAI
Descriptor: RM TEMP
Value: 70.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: 0 00 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL.OLFCU.SAS
Point Name: OL.OLFCU.SAS
Point Type: LAO
Descriptor: SUPPLY STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OL.OLFCU.SAT
Point Name: OL.OLFCU.SAT
Point Type: LAI
Descriptor: SUPPL YTEMP
Value: 54.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
Point System Name: OLIN.OLFCU.LAB306:PPCL Address
Point Name: OLIN.OLFCU.LAB306:PPCL Address
Point Type: LAI
Descriptor:
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: OLIN.LAB306
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.0
BLN04 MYERS.PENTHOUSE: Supplied Field Panel number out of range
BLN04 MYERS.LOWERLEVEL: Supplied Field Panel number out of range
Point System Name: OLDMUSIC.ELEC.MOD1:COMMERROR
Point Name: OLDMUSIC.ELEC.MOD1:COMMERROR
Object Name: OLDMUSIC.ELEC.MOD1:COMMERROR
Object ID: binary-input - 15403
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: EQS_OFF_ON
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7014
Point Address: 6 03 03
Normally Closed: No
Point System Name: OLIN.ELEC.MOD1:COMMERROR
Point Name: OLIN.ELEC.MOD1:COMMERROR
Object Name: OLIN.ELEC.MOD1:COMMERROR
Object ID: binary-input - 15603
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: EQS_OFF_ON
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Notification Class: 0
Annunciate To-Normal: No
Annunciate To-OffNormal: No
Annunciate To-Fault: No
Totalization: None
Field Panel: 7014
Point Address: 6 05 03
Normally Closed: No
BACDev_205003: 3rd party BACnet panels cannot resolve wildcards
BACDev_204003: 3rd party BACnet panels cannot resolve wildcards
LDC_EF12: 3rd party BACnet panels cannot resolve wildcards
LDC_EF03: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD8: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD9: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD5: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD6: 3rd party BACnet panels cannot resolve wildcards
ACDIN.EF02: 3rd party BACnet panels cannot resolve wildcards
ACDIN.EF04: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD1: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD2: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD3: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD4: 3rd party BACnet panels cannot resolve wildcards
ACDIN.HOOD7: 3rd party BACnet panels cannot resolve wildcards
BLN3_41: Field Panel Not In Defined Field Panel List
BLN3_70: Field Panel Not In Defined Field Panel List
BLN3_4914: Field Panel Not In Defined Field Panel List
BLN3_7000: Field Panel Not In Defined Field Panel List
********************************************************************************
******************************** End of Report *********************************

## Hulings
10/16/2017 Carleton College 02:50 PM
Panel Point Definition Report
Selection: HU.R102.DSET, HU.R102.ECFM, HU.R102.EDMP, HU.R102.ESET, ...
(1617 Points)
Point System Name: HU.R102.DSET
Point Name: HU.R102.DSET
Point Type: LAO
Descriptor: 102 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.ECFM
Point Name: HU.R102.ECFM
Point Type: LAO
Descriptor: 102 EXH CFM
Value: 108.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.EDMP
Point Name: HU.R102.EDMP
Point Type: LAO
Descriptor: 102 EXH DMPR
Value: 8.55
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R102.ESET
Point Name: HU.R102.ESET
Point Type: LAO
Descriptor: 102 EXH SET
Value: 109.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.EVPRS
Point Name: HU.R102.EVPRS
Point Type: LAI
Descriptor: 102 EXH VPSR
Value: 0.07
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R102.EXCFM
Point Name: HU.R102.EXCFM
Point Type: LAO
Descriptor: 102 EXH CFM
Value: 1.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.EXSET
Point Name: HU.R102.EXSET
Point Type: LAO
Descriptor: 102 EXH SET
Value: 1.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.FCFM
Point Name: HU.R102.FCFM
Point Type: LAI
Descriptor: 102 FUME CFM
Value: 484.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 0.96988
********************************************************************************
Point System Name: HU.R102.FDIFF
Point Name: HU.R102.FDIFF
Point Type: LAO
Descriptor: 102 FLOW DIF
Value: 205.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.MCFM
Point Name: HU.R102.MCFM
Point Type: LAO
Descriptor: 102 CFM MIN
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.MSAIR
Point Name: HU.R102.MSAIR
Point Type: LAO
Descriptor: 102MXSUPAIR
Value: 920.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.OCC
Point Name: HU.R102.OCC
Point Type: LDO
Descriptor: RM 102 OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R102.OSUP
Point Name: HU.R102.OSUP
Point Type: LAO
Descriptor: 102 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.RHV
Point Name: HU.R102.RHV
Point Type: LAO
Descriptor: 102 RH VALVE
Value: 12.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R102.RM
Point Name: HU.R102.RM
Point Type: LAI
Descriptor: 102 TEMP
Value: 72.55
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.RMT
Point Name: HU.R102.RMT
Point Type: LAI
Descriptor: 102 TEMP
Value: 72.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.RSET
Point Name: HU.R102.RSET
Point Type: LAO
Descriptor: 102 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R102.SACFM
Point Name: HU.R102.SACFM
Point Type: LAO
Descriptor: 102 SUP CFM
Value: 3.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.SASET
Point Name: HU.R102.SASET
Point Type: LAO
Descriptor: 102 SUP SET
Value: 3.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.SBIAS
Point Name: HU.R102.SBIAS
Point Type: LAO
Descriptor: 102 SUP BIAS
Value: 8.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.SCFM
Point Name: HU.R102.SCFM
Point Type: LAO
Descriptor: 102 SUP CFM
Value: 397.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.SDMP
Point Name: HU.R102.SDMP
Point Type: LAO
Descriptor: 102 SUP DMPR
Value: 8.56
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R102.SREQ
Point Name: HU.R102.SREQ
Point Type: LAO
Descriptor: 102 SUP REQ
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.SSET
Point Name: HU.R102.SSET
Point Type: LAO
Descriptor: 102 SUP SET
Value: 393.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.SVPRS
Point Name: HU.R102.SVPRS
Point Type: LAI
Descriptor: 102 SUP VPSR
Value: 0.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R102.TEXH
Point Name: HU.R102.TEXH
Point Type: LAO
Descriptor: 102 TOT EXH
Value: 594.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R102.TSUP
Point Name: HU.R102.TSUP
Point Type: LAO
Descriptor: 102 TOT SUP
Value: 402.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.DSET
Point Name: HU.R109.DSET
Point Type: LAO
Descriptor: 109 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.F2CFM
Point Name: HU.R109.F2CFM
Point Type: LAI
Descriptor: 109 FUM2 CFM
Value: 201.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.02343
Intercept: -86.19324
COV Limit: 4.86863
********************************************************************************
Point System Name: HU.R109.FDIFF
Point Name: HU.R109.FDIFF
Point Type: LAO
Descriptor: 109 FLOW DIF
Value: 201.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.OCC
Point Name: HU.R109.OCC
Point Type: LDO
Descriptor: RM 109 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R109.OSUP
Point Name: HU.R109.OSUP
Point Type: LAO
Descriptor: 109 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.RHV
Point Name: HU.R109.RHV
Point Type: LAO
Descriptor: 109 RH VALVE
Value: 7.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R109.RM
Point Name: HU.R109.RM
Point Type: LAI
Descriptor: 109 TEMP
Value: 72.17
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.RMT
Point Name: HU.R109.RMT
Point Type: LAI
Descriptor: 109 TEMP
Value: 72.17
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.RSET
Point Name: HU.R109.RSET
Point Type: LAO
Descriptor: 109 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R109.SACFM
Point Name: HU.R109.SACFM
Point Type: LAO
Descriptor: 109 SUP CFM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.SASET
Point Name: HU.R109.SASET
Point Type: LAO
Descriptor: 109 SUP SET
Value: 0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.SBIAS
Point Name: HU.R109.SBIAS
Point Type: LAO
Descriptor: 109 SUP BIAS
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.SCFM
Point Name: HU.R109.SCFM
Point Type: LAO
Descriptor: 109 SUP CFM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.SDMP
Point Name: HU.R109.SDMP
Point Type: LAO
Descriptor: 109 SUP DMPR
Value: 7.96
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R109.SSET
Point Name: HU.R109.SSET
Point Type: LAO
Descriptor: 109 SUP SET
Value: 1.37
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.SVPRS
Point Name: HU.R109.SVPRS
Point Type: LAI
Descriptor: 109 SUP VPSR
Value: -0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R109.TFH
Point Name: HU.R109.TFH
Point Type: LAO
Descriptor: 109 TOT FUME
Value: 201.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R109.TSUP
Point Name: HU.R109.TSUP
Point Type: LAO
Descriptor: 109 TOT SUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.DSET
Point Name: HU.R111.DSET
Point Type: LAO
Descriptor: 111 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.FCFM
Point Name: HU.R111.FCFM
Point Type: LAI
Descriptor: 111 FUME CFM
Value: 135.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 03
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.023984
Intercept: -146.96001
COV Limit: 4.92894
********************************************************************************
Point System Name: HU.R111.FDIFF
Point Name: HU.R111.FDIFF
Point Type: LAO
Descriptor: 111 FLOW DIF
Value: -553.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.FHCFM
Point Name: HU.R111.FHCFM
Point Type: LAI
Descriptor: R111 FH CFM
Value: 558.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 06
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.023984
Intercept: -146.96001
COV Limit: 9.9585
********************************************************************************
Point System Name: HU.R111.OCC
Point Name: HU.R111.OCC
Point Type: LDO
Descriptor: RM 111 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R111.OSUP
Point Name: HU.R111.OSUP
Point Type: LAO
Descriptor: 111 OTHERSUP
Value: 381.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.RHV
Point Name: HU.R111.RHV
Point Type: LAO
Descriptor: 111 RH VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R111.RM
Point Name: HU.R111.RM
Point Type: LAI
Descriptor: 111 TEMP
Value: 71.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.RMT
Point Name: HU.R111.RMT
Point Type: LAI
Descriptor: 111 TEMP
Value: 71.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.RSET
Point Name: HU.R111.RSET
Point Type: LAO
Descriptor: 111 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R111.SACFM
Point Name: HU.R111.SACFM
Point Type: LAO
Descriptor: 111 SUP CFM
Value: 6.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.SASET
Point Name: HU.R111.SASET
Point Type: LAO
Descriptor: 111 SUP SET
Value: 6.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.SBIAS
Point Name: HU.R111.SBIAS
Point Type: LAO
Descriptor: 111 SUP BIAS
Value: 7.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.SCFM
Point Name: HU.R111.SCFM
Point Type: LAO
Descriptor: 111 SUP CFM
Value: 322.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.SDMP
Point Name: HU.R111.SDMP
Point Type: LAO
Descriptor: 111 SUP DMPR
Value: 6.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R111.SSET
Point Name: HU.R111.SSET
Point Type: LAO
Descriptor: 111 SUP SET
Value: 694.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111.SVPRS
Point Name: HU.R111.SVPRS
Point Type: LAI
Descriptor: 111 SUP VPSR
Value: 0.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R111.TSUP
Point Name: HU.R111.TSUP
Point Type: LAO
Descriptor: 111 TOT SUP
Value: 699.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111A.FCFM
Point Name: HU.R111A.FCFM
Point Type: LAI
Descriptor: R111A FH CFM
Value: 592.35
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.033438
Intercept: -205.84
COV Limit: 9.9585
********************************************************************************
Point System Name: HU.R111A.OCC
Point Name: HU.R111A.OCC
Point Type: LDO
Descriptor: RM 111A OCCU
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R111A.OSUP
Point Name: HU.R111A.OSUP
Point Type: LAO
Descriptor: 111A OTHERSU
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111A.RM
Point Name: HU.R111A.RM
Point Type: LAI
Descriptor: 111A TEMP
Value: 66.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111A.RSET
Point Name: HU.R111A.RSET
Point Type: LAO
Descriptor: 111A RM STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R111A.SACFM
Point Name: HU.R111A.SACFM
Point Type: LAO
Descriptor: 111A SUP CFM
Value: 3.81
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111A.SCFM
Point Name: HU.R111A.SCFM
Point Type: LAO
Descriptor: 111A SUP CFM
Value: 381.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111A.SDMP
Point Name: HU.R111A.SDMP
Point Type: LAO
Descriptor: 111A SU DMPR
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R111A.SREQ
Point Name: HU.R111A.SREQ
Point Type: LAO
Descriptor: 111A SUP REQ
Value: 66.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111A.SSET
Point Name: HU.R111A.SSET
Point Type: LAO
Descriptor: 111A SUP SET
Value: 5.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R111A.SVPRS
Point Name: HU.R111A.SVPRS
Point Type: LAI
Descriptor: 111A SU VPSR
Value: 1.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: 0 00 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R111A.TSUP
Point Name: HU.R111A.TSUP
Point Type: LAO
Descriptor: 111A TOT SUP
Value: 381.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM111
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.DSET
Point Name: HU.R112.DSET
Point Type: LAO
Descriptor: 112 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.F1CFM
Point Name: HU.R112.F1CFM
Point Type: LAI
Descriptor: 112 FUM1 CFM
Value: 299.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 09
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.033789
Intercept: -208.10001
COV Limit: 4.92213
********************************************************************************
Point System Name: HU.R112.F2CFM
Point Name: HU.R112.F2CFM
Point Type: LAI
Descriptor: 112 FUM2 CFM
Value: 250.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.023688
Intercept: -87.14043
COV Limit: 4.92213
********************************************************************************
Point System Name: HU.R112.FDIFF
Point Name: HU.R112.FDIFF
Point Type: LAO
Descriptor: 112 FLOW DIF
Value: 550.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.OCC
Point Name: HU.R112.OCC
Point Type: LDO
Descriptor: RM 112 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R112.OSUP
Point Name: HU.R112.OSUP
Point Type: LAO
Descriptor: 112 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.RHV
Point Name: HU.R112.RHV
Point Type: LAO
Descriptor: 112 RH VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R112.RM
Point Name: HU.R112.RM
Point Type: LAI
Descriptor: 112 TEMP
Value: 69.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.RMT
Point Name: HU.R112.RMT
Point Type: LAI
Descriptor: 112 TEMP
Value: 69.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.RSET
Point Name: HU.R112.RSET
Point Type: LAO
Descriptor: 112 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R112.SACFM
Point Name: HU.R112.SACFM
Point Type: LAO
Descriptor: 112 SUP CFM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.SASET
Point Name: HU.R112.SASET
Point Type: LAO
Descriptor: 112 SUP SET
Value: 3.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.SBIAS
Point Name: HU.R112.SBIAS
Point Type: LAO
Descriptor: 112 SUP BIAS
Value: 6.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.SCFM
Point Name: HU.R112.SCFM
Point Type: LAO
Descriptor: 112 SUP CFM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.SDMP
Point Name: HU.R112.SDMP
Point Type: LAO
Descriptor: 112 SUP DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R112.SSET
Point Name: HU.R112.SSET
Point Type: LAO
Descriptor: 112 SUP SET
Value: 350.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.SVPRS
Point Name: HU.R112.SVPRS
Point Type: LAI
Descriptor: 112 SUP VPSR
Value: -0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R112.TFH
Point Name: HU.R112.TFH
Point Type: LAO
Descriptor: 112 TOT FUME
Value: 550.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R112.TSUP
Point Name: HU.R112.TSUP
Point Type: LAO
Descriptor: 112 TOT SUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.DSET
Point Name: HU.R121.DSET
Point Type: LAO
Descriptor: 121 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.ECFM
Point Name: HU.R121.ECFM
Point Type: LAO
Descriptor: 121 EXH CFM
Value: 272.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.EDMP
Point Name: HU.R121.EDMP
Point Type: LAO
Descriptor: 121 EXH DMPR
Value: 4.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49816
********************************************************************************
Point System Name: HU.R121.ESET
Point Name: HU.R121.ESET
Point Type: LAO
Descriptor: 121 EXH SET
Value: 270.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.EVPRS
Point Name: HU.R121.EVPRS
Point Type: LAI
Descriptor: 121 EXH VPSR
Value: 0.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R121.EXCFM
Point Name: HU.R121.EXCFM
Point Type: LAO
Descriptor: 121 EXH CFM
Value: 2.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.EXSET
Point Name: HU.R121.EXSET
Point Type: LAO
Descriptor: 121 EXH SET
Value: 2.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.FCFM
Point Name: HU.R121.FCFM
Point Type: LAI
Descriptor: 121 FUME CFM
Value: 124.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R121.FDIFF
Point Name: HU.R121.FDIFF
Point Type: LAO
Descriptor: 121 FLOW DIF
Value: -0.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.MCFM
Point Name: HU.R121.MCFM
Point Type: LAO
Descriptor: 121 CFM MIN
Value: 763.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.MSAIR
Point Name: HU.R121.MSAIR
Point Type: LAO
Descriptor: 121BMXSUPAIR
Value: 1485.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.OCC
Point Name: HU.R121.OCC
Point Type: LDO
Descriptor: 121 OCCUPIED
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R121.OSUP
Point Name: HU.R121.OSUP
Point Type: LAO
Descriptor: 121 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.RHV
Point Name: HU.R121.RHV
Point Type: LAO
Descriptor: 121 RH VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49816
********************************************************************************
Point System Name: HU.R121.RM
Point Name: HU.R121.RM
Point Type: LAI
Descriptor: 121 TEMP
Value: 70.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 0.9
********************************************************************************
Point System Name: HU.R121.RMT
Point Name: HU.R121.RMT
Point Type: LAI
Descriptor: 121 TEMP
Value: 70.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 0.9
********************************************************************************
Point System Name: HU.R121.RMTP
Point Name: HU.R121.RMTP
Point Type: LAI
Descriptor: 121 TEMP
Value: 70.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.RSET
Point Name: HU.R121.RSET
Point Type: LAO
Descriptor: 121 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R121.SACFM
Point Name: HU.R121.SACFM
Point Type: LAO
Descriptor: 121 SUP CFM
Value: 4.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.SASET
Point Name: HU.R121.SASET
Point Type: LAO
Descriptor: 121 SUP SET
Value: 3.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.SBIAS
Point Name: HU.R121.SBIAS
Point Type: LAO
Descriptor: 121 SUP BIAS
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.9
********************************************************************************
Point System Name: HU.R121.SCFM
Point Name: HU.R121.SCFM
Point Type: LAO
Descriptor: 121 SUP CFM
Value: 404.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.SDMP
Point Name: HU.R121.SDMP
Point Type: LAO
Descriptor: 121 SUP DMPR
Value: 6.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49816
********************************************************************************
Point System Name: HU.R121.SREQ
Point Name: HU.R121.SREQ
Point Type: LAO
Descriptor: 121 SUP REQ
Value: 1235.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.SSET
Point Name: HU.R121.SSET
Point Type: LAO
Descriptor: 121 SUP SET
Value: 400.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.SVPRS
Point Name: HU.R121.SVPRS
Point Type: LAI
Descriptor: 121 SUP VPSR
Value: 0.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R121.TEXH
Point Name: HU.R121.TEXH
Point Type: LAO
Descriptor: 121 TOT EXH
Value: 399.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121.TSUP
Point Name: HU.R121.TSUP
Point Type: LAO
Descriptor: 121 TOT SUP
Value: 402.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.DSET
Point Name: HU.R121B.DSET
Point Type: LAO
Descriptor: 121B DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.ECFM
Point Name: HU.R121B.ECFM
Point Type: LAO
Descriptor: 121B EXH CFM
Value: 430.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.EDMP
Point Name: HU.R121B.EDMP
Point Type: LAO
Descriptor: 121B EX DMPR
Value: 7.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49816
********************************************************************************
Point System Name: HU.R121B.ESET
Point Name: HU.R121B.ESET
Point Type: LAO
Descriptor: 121B EXH SET
Value: 399.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.EVPRS
Point Name: HU.R121B.EVPRS
Point Type: LAI
Descriptor: 121B EX VPSR
Value: 0.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R121B.EXCFM
Point Name: HU.R121B.EXCFM
Point Type: LAO
Descriptor: 121B EXH CFM
Value: 4.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.EXSET
Point Name: HU.R121B.EXSET
Point Type: LAO
Descriptor: 121D EXH SET
Value: 4.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.FCFM
Point Name: HU.R121B.FCFM
Point Type: LAI
Descriptor: 121B FUM CFM
Value: 490.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 11
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R121B.FDIFF
Point Name: HU.R121B.FDIFF
Point Type: LAO
Descriptor: 121B FLO DIF
Value: 29.17
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.MCFM
Point Name: HU.R121B.MCFM
Point Type: LAO
Descriptor: 121B CFM MIN
Value: 665.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.MSAIR
Point Name: HU.R121B.MSAIR
Point Type: LAO
Descriptor: 121MXSUPAIR
Value: 1235.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.OCC
Point Name: HU.R121B.OCC
Point Type: LDO
Descriptor: 121B OCCUPIE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R121B.OSUP
Point Name: HU.R121B.OSUP
Point Type: LAO
Descriptor: 121B OTHERSU
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.RHV
Point Name: HU.R121B.RHV
Point Type: LAO
Descriptor: 121B RH VLV
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49816
********************************************************************************
Point System Name: HU.R121B.RM
Point Name: HU.R121B.RM
Point Type: LAI
Descriptor: 121B TEMP
Value: 70.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 0.9
********************************************************************************
Point System Name: HU.R121B.RMT
Point Name: HU.R121B.RMT
Point Type: LAI
Descriptor: 121B TEMP
Value: 70.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 0.9
********************************************************************************
Point System Name: HU.R121B.RMTP
Point Name: HU.R121B.RMTP
Point Type: LAI
Descriptor: 121B TEMP
Value: 70.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.RSET
Point Name: HU.R121B.RSET
Point Type: LAO
Descriptor: 121B RM STPT
Value: 70.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R121B.SACFM
Point Name: HU.R121B.SACFM
Point Type: LAO
Descriptor: 121B SUP CFM
Value: 8.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.SASET
Point Name: HU.R121B.SASET
Point Type: LAO
Descriptor: 121B SUP SET
Value: 8.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.SBIAS
Point Name: HU.R121B.SBIAS
Point Type: LAO
Descriptor: 121B SU BIAS
Value: 7.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.9
********************************************************************************
Point System Name: HU.R121B.SCFM
Point Name: HU.R121B.SCFM
Point Type: LAO
Descriptor: 121B SUP CFM
Value: 899.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.SDMP
Point Name: HU.R121B.SDMP
Point Type: LAO
Descriptor: 121B SU DMPR
Value: 5.81
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49816
********************************************************************************
Point System Name: HU.R121B.SREQ
Point Name: HU.R121B.SREQ
Point Type: LAO
Descriptor: 121B SUP REQ
Value: 890.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.SSET
Point Name: HU.R121B.SSET
Point Type: LAO
Descriptor: 121B SUP SET
Value: 881.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.SVPRS
Point Name: HU.R121B.SVPRS
Point Type: LAI
Descriptor: 121B SU VPSR
Value: 0.53
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R121B.TEXH
Point Name: HU.R121B.TEXH
Point Type: LAO
Descriptor: 121B TOT EXH
Value: 877.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R121B.TSUP
Point Name: HU.R121B.TSUP
Point Type: LAO
Descriptor: 121B TOT SUP
Value: 894.55
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM121
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.OCC
Point Name: HU.R1AA.OCC
Point Type: LDO
Descriptor: RM 1AA OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R1AA.OSUP
Point Name: HU.R1AA.OSUP
Point Type: LAO
Descriptor: 1AA OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.RHV
Point Name: HU.R1AA.RHV
Point Type: LAO
Descriptor: 1AA RH VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R1AA.RM
Point Name: HU.R1AA.RM
Point Type: LAI
Descriptor: 1AA TEMP
Value: 66.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.RMT
Point Name: HU.R1AA.RMT
Point Type: LAI
Descriptor: 1AA TEMP
Value: 66.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.RSET
Point Name: HU.R1AA.RSET
Point Type: LAO
Descriptor: 1AA RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R1AA.SACFM
Point Name: HU.R1AA.SACFM
Point Type: LAO
Descriptor: 1AA SUP CFM
Value: 16.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.SASET
Point Name: HU.R1AA.SASET
Point Type: LAO
Descriptor: 1AA SUP SET
Value: 17.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.SCFM
Point Name: HU.R1AA.SCFM
Point Type: LAO
Descriptor: 1AA SUP CFM
Value: 1682.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.SDMP
Point Name: HU.R1AA.SDMP
Point Type: LAO
Descriptor: 1AA SUP DMPR
Value: 4.91
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R1AA.SREQ
Point Name: HU.R1AA.SREQ
Point Type: LAO
Descriptor: 1AA SUP REQ
Value: 1725.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AA.SVPRS
Point Name: HU.R1AA.SVPRS
Point Type: LAI
Descriptor: 1AA SUP VPSR
Value: 0.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R1AA.TSUP
Point Name: HU.R1AA.TSUP
Point Type: LAO
Descriptor: 1AA TOT SUP
Value: 1706.83
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM101
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.OCC
Point Name: HU.R1AC.OCC
Point Type: LDO
Descriptor: RM 1AC OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R1AC.OSUP
Point Name: HU.R1AC.OSUP
Point Type: LAO
Descriptor: 1AC OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.RM
Point Name: HU.R1AC.RM
Point Type: LAI
Descriptor: 1AC TEMP
Value: 68.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.RMT
Point Name: HU.R1AC.RMT
Point Type: LAI
Descriptor: 1AC TEMP
Value: 68.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.RSET
Point Name: HU.R1AC.RSET
Point Type: LAO
Descriptor: 1AC RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R1AC.SACFM
Point Name: HU.R1AC.SACFM
Point Type: LAO
Descriptor: 1AC SUP CFM
Value: 0.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.SASET
Point Name: HU.R1AC.SASET
Point Type: LAO
Descriptor: 1AC SUP SET
Value: 0.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.SCFM
Point Name: HU.R1AC.SCFM
Point Type: LAO
Descriptor: 1AC SUP CFM
Value: 44.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.SDMP
Point Name: HU.R1AC.SDMP
Point Type: LAO
Descriptor: 1AC SUP DMPR
Value: 9.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R1AC.SSET
Point Name: HU.R1AC.SSET
Point Type: LAO
Descriptor: 1AC SUP SET
Value: 45.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AC.SVPRS
Point Name: HU.R1AC.SVPRS
Point Type: LAI
Descriptor: 1AC SUP VPSR
Value: 0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R1AC.TSUP
Point Name: HU.R1AC.TSUP
Point Type: LAO
Descriptor: 1AC TOT SUP
Value: 45.53
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM122
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AG.OCC
Point Name: HU.R1AG.OCC
Point Type: LDO
Descriptor: RM 1AG OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R1AG.OSUP
Point Name: HU.R1AG.OSUP
Point Type: LAO
Descriptor: 1AG OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AG.RM
Point Name: HU.R1AG.RM
Point Type: LAI
Descriptor: 1AG TEMP
Value: 68.49
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AG.RSET
Point Name: HU.R1AG.RSET
Point Type: LAO
Descriptor: 1AG RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R1AG.SACFM
Point Name: HU.R1AG.SACFM
Point Type: LAO
Descriptor: 1AG SUP CFM
Value: 4.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AG.SCFM
Point Name: HU.R1AG.SCFM
Point Type: LAO
Descriptor: 1AG SUP CFM
Value: 404.56
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AG.SDMP
Point Name: HU.R1AG.SDMP
Point Type: LAO
Descriptor: 1AG SUP DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R1AG.SREQ
Point Name: HU.R1AG.SREQ
Point Type: LAO
Descriptor: 1AG SUP REQ
Value: 45.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AG.SSET
Point Name: HU.R1AG.SSET
Point Type: LAO
Descriptor: 1AG SUP SET
Value: 0.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AG.SVPRS
Point Name: HU.R1AG.SVPRS
Point Type: LAI
Descriptor: 1AG SUP VPSR
Value: 1.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R1AG.TSUP
Point Name: HU.R1AG.TSUP
Point Type: LAO
Descriptor: 1AG TOT SUP
Value: 404.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.OCC
Point Name: HU.R1AH.OCC
Point Type: LDO
Descriptor: RM 1AH OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R1AH.OSUP
Point Name: HU.R1AH.OSUP
Point Type: LAO
Descriptor: 1AH OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.RHV
Point Name: HU.R1AH.RHV
Point Type: LAO
Descriptor: 1AH RH VALVE
Value: 12.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R1AH.RM
Point Name: HU.R1AH.RM
Point Type: LAI
Descriptor: 1AH TEMP
Value: 69.37
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.RMT
Point Name: HU.R1AH.RMT
Point Type: LAI
Descriptor: 1AH TEMP
Value: 69.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.RSET
Point Name: HU.R1AH.RSET
Point Type: LAO
Descriptor: 1AH RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R1AH.SACFM
Point Name: HU.R1AH.SACFM
Point Type: LAO
Descriptor: 1AH SUP CFM
Value: 1.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.SCFM
Point Name: HU.R1AH.SCFM
Point Type: LAO
Descriptor: 1AH SUP CFM
Value: 174.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.SDMP
Point Name: HU.R1AH.SDMP
Point Type: LAO
Descriptor: 1AH SUP DMPR
Value: 7.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R1AH.SREQ
Point Name: HU.R1AH.SREQ
Point Type: LAO
Descriptor: 1AH SUP REQ
Value: 177.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.SSET
Point Name: HU.R1AH.SSET
Point Type: LAO
Descriptor: 1AH SUP SET
Value: 1.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R1AH.SVPRS
Point Name: HU.R1AH.SVPRS
Point Type: LAI
Descriptor: 1AH SUP VPSR
Value: 0.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R1AH.TSUP
Point Name: HU.R1AH.TSUP
Point Type: LAO
Descriptor: 1AH SUP CFM
Value: 174.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM112
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.DSET
Point Name: HU.R202.DSET
Point Type: LAO
Descriptor: 202 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.ECFM
Point Name: HU.R202.ECFM
Point Type: LAO
Descriptor: 202 EXH CFM
Value: 1121.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.EDMP
Point Name: HU.R202.EDMP
Point Type: LAO
Descriptor: 202 EXH DMPR
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R202.ESET
Point Name: HU.R202.ESET
Point Type: LAO
Descriptor: 202 EXH SET
Value: 1130.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.EVPRS
Point Name: HU.R202.EVPRS
Point Type: LAI
Descriptor: 202 EXH VPSR
Value: 0.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R202.EXCFM
Point Name: HU.R202.EXCFM
Point Type: LAO
Descriptor: 202 EXH CFM
Value: 11.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.EXSET
Point Name: HU.R202.EXSET
Point Type: LAO
Descriptor: 202 EXH SET
Value: 11.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.FCFM
Point Name: HU.R202.FCFM
Point Type: LAI
Descriptor: 202 FUME CFM
Value: 125.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R202.FDIFF
Point Name: HU.R202.FDIFF
Point Type: LAO
Descriptor: 202 FLOW DIF
Value: 316.26
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.MCFM
Point Name: HU.R202.MCFM
Point Type: LAO
Descriptor: 202 CFM MIN
Value: 767.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.MSAIR
Point Name: HU.R202.MSAIR
Point Type: LAO
Descriptor: 202MXSUPAIR
Value: 1260.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.OCC
Point Name: HU.R202.OCC
Point Type: LDO
Descriptor: RM 202 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R202.OSUP
Point Name: HU.R202.OSUP
Point Type: LAO
Descriptor: 202 OTHERSUP
Value: 84.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.RHV
Point Name: HU.R202.RHV
Point Type: LAO
Descriptor: 202 RH VALVE
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R202.RM
Point Name: HU.R202.RM
Point Type: LAI
Descriptor: 202 TEMP
Value: 69.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.40962
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.RMT
Point Name: HU.R202.RMT
Point Type: LAI
Descriptor: 202 TEMP
Value: 70.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.RSET
Point Name: HU.R202.RSET
Point Type: LAO
Descriptor: 202 RM SETPT
Value: 70.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R202.SACFM
Point Name: HU.R202.SACFM
Point Type: LAO
Descriptor: 202 SUP CFM
Value: 10.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.SASET
Point Name: HU.R202.SASET
Point Type: LAO
Descriptor: 202 SUP SET
Value: 10.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.SBIAS
Point Name: HU.R202.SBIAS
Point Type: LAO
Descriptor: 202 SU BIAS
Value: 6.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.SCFM
Point Name: HU.R202.SCFM
Point Type: LAO
Descriptor: 202 SUP CFM
Value: 990.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.SDMP
Point Name: HU.R202.SDMP
Point Type: LAO
Descriptor: 202 SUP DMPR
Value: 6.49
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R202.SREQ
Point Name: HU.R202.SREQ
Point Type: LAO
Descriptor: 202 SUP REQ
Value: 1260.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.SSET
Point Name: HU.R202.SSET
Point Type: LAO
Descriptor: 202 SUP SET
Value: 1034.83
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.SVPRS
Point Name: HU.R202.SVPRS
Point Type: LAI
Descriptor: 202 SUP VPSR
Value: 0.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R202.TEXH
Point Name: HU.R202.TEXH
Point Type: LAO
Descriptor: 202 TOT EXH
Value: 1255.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R202.TSUP
Point Name: HU.R202.TSUP
Point Type: LAO
Descriptor: 202 TOT SUP
Value: 1048.47
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.DSET
Point Name: HU.R203.DSET
Point Type: LAO
Descriptor: 203 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.ECFM
Point Name: HU.R203.ECFM
Point Type: LAO
Descriptor: 203 EXH CFM
Value: 496.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.EDMP
Point Name: HU.R203.EDMP
Point Type: LAO
Descriptor: 203 EXH DMPR
Value: 7.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R203.ESET
Point Name: HU.R203.ESET
Point Type: LAO
Descriptor: 203 EXH SET
Value: 486.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.EVPRS
Point Name: HU.R203.EVPRS
Point Type: LAI
Descriptor: 203 EXH VPSR
Value: 0.07
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R203.EXCFM
Point Name: HU.R203.EXCFM
Point Type: LAO
Descriptor: 203 EXH CFM
Value: 4.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.EXSET
Point Name: HU.R203.EXSET
Point Type: LAO
Descriptor: 203 EXH SET
Value: 4.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.FCFM
Point Name: HU.R203.FCFM
Point Type: LAI
Descriptor: 203 FUME CFM
Value: 125.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 06
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R203.FDIFF
Point Name: HU.R203.FDIFF
Point Type: LAO
Descriptor: 203 FLOW DIF
Value: 48.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.MCFM
Point Name: HU.R203.MCFM
Point Type: LAO
Descriptor: 203 CFM MIN
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.MSAIR
Point Name: HU.R203.MSAIR
Point Type: LAO
Descriptor: 203MXSUPAIR
Value: 1683.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.OCC
Point Name: HU.R203.OCC
Point Type: LDO
Descriptor: RM 203 OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R203.OSUP
Point Name: HU.R203.OSUP
Point Type: LAO
Descriptor: 203 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.RHV
Point Name: HU.R203.RHV
Point Type: LAO
Descriptor: 203 RH VALVE
Value: 8.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R203.RM
Point Name: HU.R203.RM
Point Type: LAI
Descriptor: 203 TEMP
Value: 64.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.RMT
Point Name: HU.R203.RMT
Point Type: LAI
Descriptor: 203 TEMP
Value: 64.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.RSET
Point Name: HU.R203.RSET
Point Type: LAO
Descriptor: 203 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R203.SACFM
Point Name: HU.R203.SACFM
Point Type: LAO
Descriptor: 203 SUP CFM
Value: 5.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.SASET
Point Name: HU.R203.SASET
Point Type: LAO
Descriptor: 203 SUP SET
Value: 4.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.SBIAS
Point Name: HU.R203.SBIAS
Point Type: LAO
Descriptor: 203 SU BIAS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.SCFM
Point Name: HU.R203.SCFM
Point Type: LAO
Descriptor: 203 SUP CFM
Value: 595.32
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.SDMP
Point Name: HU.R203.SDMP
Point Type: LAO
Descriptor: 203 SUP DMPR
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R203.SREQ
Point Name: HU.R203.SREQ
Point Type: LAO
Descriptor: 203 SUP REQ
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.SSET
Point Name: HU.R203.SSET
Point Type: LAO
Descriptor: 203 SUP SET
Value: 413.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.SVPRS
Point Name: HU.R203.SVPRS
Point Type: LAI
Descriptor: 203 SUP VPSR
Value: 0.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R203.TEXH
Point Name: HU.R203.TEXH
Point Type: LAO
Descriptor: 203 TOT EXH
Value: 617.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203.TSUP
Point Name: HU.R203.TSUP
Point Type: LAO
Descriptor: 203 TOT SUP
Value: 588.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.DSET
Point Name: HU.R203A.DSET
Point Type: LAO
Descriptor: 203A DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.ECFM
Point Name: HU.R203A.ECFM
Point Type: LAO
Descriptor: 203A EXH CFM
Value: 404.07
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.EDMP
Point Name: HU.R203A.EDMP
Point Type: LAO
Descriptor: 203A EX DMPR
Value: 6.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R203A.ESET
Point Name: HU.R203A.ESET
Point Type: LAO
Descriptor: 203A EXH SET
Value: 407.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.EVPRS
Point Name: HU.R203A.EVPRS
Point Type: LAI
Descriptor: 203A EX VPSR
Value: 0.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R203A.EXCFM
Point Name: HU.R203A.EXCFM
Point Type: LAO
Descriptor: 203A EXH CFM
Value: 4.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.FCFM
Point Name: HU.R203A.FCFM
Point Type: LAI
Descriptor: 203A FUM CFM
Value: 204.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 06
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 9.976
********************************************************************************
Point System Name: HU.R203A.FDIFF
Point Name: HU.R203A.FDIFF
Point Type: LAO
Descriptor: 203A FLW DIF
Value: 198.53
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.MCFM
Point Name: HU.R203A.MCFM
Point Type: LAO
Descriptor: 203A CFM MIN
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.MSAIR
Point Name: HU.R203A.MSAIR
Point Type: LAO
Descriptor: 203AMXSUPAIR
Value: 1452.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.OCC
Point Name: HU.R203A.OCC
Point Type: LDO
Descriptor: RM 203A OCCU
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R203A.OSUP
Point Name: HU.R203A.OSUP
Point Type: LAI
Descriptor: 203A OTHERSU
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.RHV
Point Name: HU.R203A.RHV
Point Type: LAO
Descriptor: 203A RH VLV
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R203A.RM
Point Name: HU.R203A.RM
Point Type: LAI
Descriptor: 203A TEMP
Value: 65.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.RMT
Point Name: HU.R203A.RMT
Point Type: LAI
Descriptor: 203A TEMP
Value: 65.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.RSET
Point Name: HU.R203A.RSET
Point Type: LAO
Descriptor: 203A RM STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R203A.SACFM
Point Name: HU.R203A.SACFM
Point Type: LAO
Descriptor: 203A SUP CFM
Value: 4.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.SASET
Point Name: HU.R203A.SASET
Point Type: LAO
Descriptor: 203A SUP SET
Value: 4.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.SBIAS
Point Name: HU.R203A.SBIAS
Point Type: LAO
Descriptor: 203A SU BIAS
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.SCFM
Point Name: HU.R203A.SCFM
Point Type: LAO
Descriptor: 203A SUP CFM
Value: 405.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.SDMP
Point Name: HU.R203A.SDMP
Point Type: LAO
Descriptor: 203A SU DMPR
Value: 6.42
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R203A.SREQ
Point Name: HU.R203A.SREQ
Point Type: LAO
Descriptor: 203A SUP REQ
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.SSET
Point Name: HU.R203A.SSET
Point Type: LAO
Descriptor: 203A SUP SET
Value: 415.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.SVPRS
Point Name: HU.R203A.SVPRS
Point Type: LAI
Descriptor: 203A SU VPSR
Value: 0.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R203A.TCFM
Point Name: HU.R203A.TCFM
Point Type: LAI
Descriptor: 203A TOT SUP
Value: 409.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R203A.TEXH
Point Name: HU.R203A.TEXH
Point Type: LAO
Descriptor: 203A TOT EXH
Value: 617.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.DSET
Point Name: HU.R206.DSET
Point Type: LAO
Descriptor: 206 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.ECFM
Point Name: HU.R206.ECFM
Point Type: LAO
Descriptor: 206 EXH CFM
Value: 494.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.EDMP
Point Name: HU.R206.EDMP
Point Type: LAO
Descriptor: 206 EXH DMPR
Value: 7.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R206.ESET
Point Name: HU.R206.ESET
Point Type: LAO
Descriptor: 206 EXH SET
Value: 477.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.EVPRS
Point Name: HU.R206.EVPRS
Point Type: LAI
Descriptor: 206 EXH VPSR
Value: 0.07
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R206.EXCFM
Point Name: HU.R206.EXCFM
Point Type: LAO
Descriptor: 206 EXH CFM
Value: 4.83
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.EXSET
Point Name: HU.R206.EXSET
Point Type: LAO
Descriptor: 206 EXH SET
Value: 4.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.FCFM
Point Name: HU.R206.FCFM
Point Type: LAI
Descriptor: 206 FUME CFM
Value: 134.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 11
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.017448
Intercept: -54.0
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R206.FDIFF
Point Name: HU.R206.FDIFF
Point Type: LAO
Descriptor: 206 FLOW DIF
Value: 285.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.MCFM
Point Name: HU.R206.MCFM
Point Type: LAO
Descriptor: 206 CFM MIN
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.MSAIR
Point Name: HU.R206.MSAIR
Point Type: LAO
Descriptor: 206MXSUPAIR
Value: 1270.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.OCC
Point Name: HU.R206.OCC
Point Type: LDO
Descriptor: RM 206 OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R206.OSUP
Point Name: HU.R206.OSUP
Point Type: LAO
Descriptor: 206 OTHERSUP
Value: 88.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.RHV
Point Name: HU.R206.RHV
Point Type: LAO
Descriptor: 206 RH VALVE
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R206.RM
Point Name: HU.R206.RM
Point Type: LAI
Descriptor: 206 TEMP
Value: 68.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.RMT
Point Name: HU.R206.RMT
Point Type: LAI
Descriptor: 206 TEMP
Value: 68.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.RSET
Point Name: HU.R206.RSET
Point Type: LAO
Descriptor: 206 RM SETPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R206.SACFM
Point Name: HU.R206.SACFM
Point Type: LAO
Descriptor: 206 SUP CFM
Value: 4.07
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.SASET
Point Name: HU.R206.SASET
Point Type: LAO
Descriptor: 206 SUP SET
Value: 4.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.SBIAS
Point Name: HU.R206.SBIAS
Point Type: LAO
Descriptor: 206 SU BIAS
Value: 6.07
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.SCFM
Point Name: HU.R206.SCFM
Point Type: LAO
Descriptor: 206 SUP CFM
Value: 321.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.SDMP
Point Name: HU.R206.SDMP
Point Type: LAO
Descriptor: 206 SUP DMPR
Value: 6.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R206.SREQ
Point Name: HU.R206.SREQ
Point Type: LAO
Descriptor: 206 SUP REQ
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.SSET
Point Name: HU.R206.SSET
Point Type: LAO
Descriptor: 206 SUP SET
Value: 396.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.SVPRS
Point Name: HU.R206.SVPRS
Point Type: LAI
Descriptor: 206 SUP VPSR
Value: 0.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R206.TEXH
Point Name: HU.R206.TEXH
Point Type: LAO
Descriptor: 206 TOT EXH
Value: 605.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R206.TSUP
Point Name: HU.R206.TSUP
Point Type: LAO
Descriptor: 206 TOT SUP
Value: 409.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM202
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.DSET
Point Name: HU.R207.DSET
Point Type: LAO
Descriptor: 207 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.ESET
Point Name: HU.R207.ESET
Point Type: LAO
Descriptor: 207 EXH SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.EXSET
Point Name: HU.R207.EXSET
Point Type: LAO
Descriptor: 203A EXH SET
Value: 4.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.FCFM
Point Name: HU.R207.FCFM
Point Type: LAI
Descriptor: 207 FUME CFM
Value: 79.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 09
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.023984
Intercept: -359.95999
COV Limit: 4.93997
********************************************************************************
Point System Name: HU.R207.FDIFF
Point Name: HU.R207.FDIFF
Point Type: LAO
Descriptor: 207 FLOW DIF
Value: -3.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.OCC
Point Name: HU.R207.OCC
Point Type: LDO
Descriptor: RM 207 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R207.OSUP
Point Name: HU.R207.OSUP
Point Type: LAO
Descriptor: 207 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.RHV
Point Name: HU.R207.RHV
Point Type: LAO
Descriptor: 207 RH VALVE
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R207.RM
Point Name: HU.R207.RM
Point Type: LAI
Descriptor: 207 TEMP
Value: 75.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.RMT
Point Name: HU.R207.RMT
Point Type: LAI
Descriptor: 207 TEMP
Value: 75.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.RSET
Point Name: HU.R207.RSET
Point Type: LAO
Descriptor: 207 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R207.SACFM
Point Name: HU.R207.SACFM
Point Type: LAO
Descriptor: 207 SUP CFM
Value: 0.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.SASET
Point Name: HU.R207.SASET
Point Type: LAO
Descriptor: 207 SUP SET
Value: 0.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.SBIAS
Point Name: HU.R207.SBIAS
Point Type: LAO
Descriptor: 207 SUP BIAS
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.SCFM
Point Name: HU.R207.SCFM
Point Type: LAO
Descriptor: 207 SUP CFM
Value: 75.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.SDMP
Point Name: HU.R207.SDMP
Point Type: LAO
Descriptor: 207 SUP DMPR
Value: 7.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R207.SSET
Point Name: HU.R207.SSET
Point Type: LAO
Descriptor: 207 SUP SET
Value: 79.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R207.SVPRS
Point Name: HU.R207.SVPRS
Point Type: LAI
Descriptor: 207 SUP VPSR
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: 0 00 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R207.TCFM
Point Name: HU.R207.TCFM
Point Type: LAO
Descriptor: 207 TOT SUP
Value: 63.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203A
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.DSET
Point Name: HU.R212.DSET
Point Type: LAO
Descriptor: 212 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.F1CFM
Point Name: HU.R212.F1CFM
Point Type: LAI
Descriptor: 212 FUM1 CFM
Value: 208.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 05
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.033672
Intercept: -207.67999
COV Limit: 4.89523
********************************************************************************
Point System Name: HU.R212.FDIFF
Point Name: HU.R212.FDIFF
Point Type: LAO
Descriptor: 212 FLOW DIF
Value: 87.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.OCC
Point Name: HU.R212.OCC
Point Type: LDO
Descriptor: RM 212 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R212.OSUP
Point Name: HU.R212.OSUP
Point Type: LAO
Descriptor: 212 OTHERSUP
Value: 88.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.RHV
Point Name: HU.R212.RHV
Point Type: LAO
Descriptor: 212 RH VALVE
Value: 11.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R212.RM
Point Name: HU.R212.RM
Point Type: LAI
Descriptor: 212 TEMP
Value: 72.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.RMT
Point Name: HU.R212.RMT
Point Type: LAI
Descriptor: 212 TEMP
Value: 72.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.RSET
Point Name: HU.R212.RSET
Point Type: LAO
Descriptor: 212 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R212.SACFM
Point Name: HU.R212.SACFM
Point Type: LAO
Descriptor: 212 SUP CFM
Value: 2.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.SASET
Point Name: HU.R212.SASET
Point Type: LAO
Descriptor: 212 SUP SET
Value: 2.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.SBIAS
Point Name: HU.R212.SBIAS
Point Type: LAO
Descriptor: 212 SUP BIAS
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.SCFM
Point Name: HU.R212.SCFM
Point Type: LAO
Descriptor: 212 SUP CFM
Value: 121.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.SDMP
Point Name: HU.R212.SDMP
Point Type: LAO
Descriptor: 212 SUP DMPR
Value: 9.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R212.SSET
Point Name: HU.R212.SSET
Point Type: LAO
Descriptor: 212 SUP SET
Value: 208.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.SVPRS
Point Name: HU.R212.SVPRS
Point Type: LAI
Descriptor: 212 SUP VPSR
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R212.TEXH
Point Name: HU.R212.TEXH
Point Type: LAO
Descriptor: 212 TOT EXH
Value: 208.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R212.TSUP
Point Name: HU.R212.TSUP
Point Type: LAO
Descriptor: 212 TOT SUP
Value: 208.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.DSET
Point Name: HU.R213.DSET
Point Type: LAO
Descriptor: 213 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.ECFM
Point Name: HU.R213.ECFM
Point Type: LAO
Descriptor: 213 EXH CFM
Value: 77.56
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.EDMP
Point Name: HU.R213.EDMP
Point Type: LAO
Descriptor: 213 EXH DMPR
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R213.ESET
Point Name: HU.R213.ESET
Point Type: LAO
Descriptor: 213 EXH SET
Value: 1514.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.ESVPRS
Point Name: HU.R213.ESVPRS
Point Type: LAI
Descriptor: 213 EXH VPSR
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R213.EXCFM
Point Name: HU.R213.EXCFM
Point Type: LAO
Descriptor: 213 EXH CFM
Value: 0.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.EXSET
Point Name: HU.R213.EXSET
Point Type: LAO
Descriptor: 213 EXH SET
Value: 15.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.FCFM
Point Name: HU.R213.FCFM
Point Type: LAI
Descriptor: 213 FUME CFM
Value: 124.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R213.FDIFF
Point Name: HU.R213.FDIFF
Point Type: LAO
Descriptor: 213 FLOW DIF
Value: 158.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.MCFM
Point Name: HU.R213.MCFM
Point Type: LAO
Descriptor: 213 CFM MIN
Value: 788.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.MSAIR
Point Name: HU.R213.MSAIR
Point Type: LAO
Descriptor: 213MXSUPAIR
Value: 1440.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.OCC
Point Name: HU.R213.OCC
Point Type: LDO
Descriptor: RM 213 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R213.OSUP
Point Name: HU.R213.OSUP
Point Type: LAO
Descriptor: 213 OTHERSUP
Value: 44.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.RHV
Point Name: HU.R213.RHV
Point Type: LAO
Descriptor: 213 RH VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R213.RM
Point Name: HU.R213.RM
Point Type: LAI
Descriptor: 213 TEMP
Value: 69.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.RMT
Point Name: HU.R213.RMT
Point Type: LAI
Descriptor: 213 TEMP
Value: 69.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.RSET
Point Name: HU.R213.RSET
Point Type: LAO
Descriptor: 213 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R213.SACFM
Point Name: HU.R213.SACFM
Point Type: LAO
Descriptor: 213 SUP CFM
Value: 0.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.SASET
Point Name: HU.R213.SASET
Point Type: LAO
Descriptor: 213 SUP SET
Value: 0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.SBIAS
Point Name: HU.R213.SBIAS
Point Type: LAO
Descriptor: 213 SU BIAS
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.SCFM
Point Name: HU.R213.SCFM
Point Type: LAO
Descriptor: 213 SUP CFM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.SDMP
Point Name: HU.R213.SDMP
Point Type: LAO
Descriptor: 213 SUP DMPR
Value: 12.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R213.SREQ
Point Name: HU.R213.SREQ
Point Type: LAO
Descriptor: 213 SUP REQ
Value: 1440.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.SSET
Point Name: HU.R213.SSET
Point Type: LAO
Descriptor: 213 SUP SET
Value: 1.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.SVPRS
Point Name: HU.R213.SVPRS
Point Type: LAI
Descriptor: 213 SUP VPSR
Value: -0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R213.TEXH
Point Name: HU.R213.TEXH
Point Type: LAO
Descriptor: 213 TOT EXH
Value: 202.37
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213.TSUP
Point Name: HU.R213.TSUP
Point Type: LAO
Descriptor: 213 TOT SUP
Value: 44.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.DSET
Point Name: HU.R213B.DSET
Point Type: LAO
Descriptor: 213B DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.ECFM
Point Name: HU.R213B.ECFM
Point Type: LAO
Descriptor: 213B EXH CFM
Value: 403.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.EDMP
Point Name: HU.R213B.EDMP
Point Type: LAO
Descriptor: 213B EX DMPR
Value: 8.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R213B.ESET
Point Name: HU.R213B.ESET
Point Type: LAO
Descriptor: 213B EXH SET
Value: 404.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.EVPRS
Point Name: HU.R213B.EVPRS
Point Type: LAI
Descriptor: 213B EX VPSR
Value: 0.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 09
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R213B.EXCFM
Point Name: HU.R213B.EXCFM
Point Type: LAO
Descriptor: 213B EXH CFM
Value: 4.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.EXSET
Point Name: HU.R213B.EXSET
Point Type: LAO
Descriptor: 213B EXH SET
Value: 4.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.FDIFF
Point Name: HU.R213B.FDIFF
Point Type: LAO
Descriptor: 213B FLW DIF
Value: 197.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.MSAIR
Point Name: HU.R213B.MSAIR
Point Type: LAO
Descriptor: 213BMXSUPAIR
Value: 680.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.NACDMP
Point Name: HU.R213B.NACDMP
Point Type: LDO
Descriptor: NO ACLV DMPR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 21
Inverted: No
********************************************************************************
Point System Name: HU.R213B.NACRMT
Point Name: HU.R213B.NACRMT
Point Type: LAI
Descriptor: ACLV RM TEMP
Value: 73.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 10
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.NACSWT
Point Name: HU.R213B.NACSWT
Point Type: LDI
Descriptor: NO ACLV SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 01
Normally Closed: No
********************************************************************************
Point System Name: HU.R213B.OCC
Point Name: HU.R213B.OCC
Point Type: LDO
Descriptor: RM 213B OCCU
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R213B.OSUP
Point Name: HU.R213B.OSUP
Point Type: LAO
Descriptor: 213B OTHERSU
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.RHV
Point Name: HU.R213B.RHV
Point Type: LAO
Descriptor: 213B RH VLV
Value: 8.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R213B.RM
Point Name: HU.R213B.RM
Point Type: LAI
Descriptor: 213B TEMP
Value: 71.96
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.RMT
Point Name: HU.R213B.RMT
Point Type: LAI
Descriptor: 213B TEMP
Value: 71.96
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.RSET
Point Name: HU.R213B.RSET
Point Type: LAO
Descriptor: 213B RM SETP
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R213B.SACDMP
Point Name: HU.R213B.SACDMP
Point Type: LDO
Descriptor: SO ACLV DMPR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 20
Inverted: No
********************************************************************************
Point System Name: HU.R213B.SACFM
Point Name: HU.R213B.SACFM
Point Type: LAO
Descriptor: 213B SUP CFM
Value: 2.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.SACSWT
Point Name: HU.R213B.SACSWT
Point Type: LDI
Descriptor: SO ACLV SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 02
Normally Closed: No
********************************************************************************
Point System Name: HU.R213B.SASET
Point Name: HU.R213B.SASET
Point Type: LAO
Descriptor: 213B SUP SET
Value: 1.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.SCFM
Point Name: HU.R213B.SCFM
Point Type: LAO
Descriptor: 213B SUP CFM
Value: 204.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.SDMP
Point Name: HU.R213B.SDMP
Point Type: LAO
Descriptor: 213B SUP DPR
Value: 7.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R213B.SREQ
Point Name: HU.R213B.SREQ
Point Type: LAO
Descriptor: 213B SUP REQ
Value: 204.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.SSET
Point Name: HU.R213B.SSET
Point Type: LAO
Descriptor: 213B SUP SET
Value: 207.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R213B.SVPRS
Point Name: HU.R213B.SVPRS
Point Type: LAI
Descriptor: 213B SU VPSR
Value: 0.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R213B.TSUP
Point Name: HU.R213B.TSUP
Point Type: LAO
Descriptor: 213B TOT SUP
Value: 202.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.DSET
Point Name: HU.R215.DSET
Point Type: LAO
Descriptor: 215 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.ECFM
Point Name: HU.R215.ECFM
Point Type: LAO
Descriptor: 215 EXH CFM
Value: 484.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.EDMP
Point Name: HU.R215.EDMP
Point Type: LAO
Descriptor: 215 EXH DMPR
Value: 7.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R215.ESET
Point Name: HU.R215.ESET
Point Type: LAO
Descriptor: 215 EXH SET
Value: 484.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.EVPRS
Point Name: HU.R215.EVPRS
Point Type: LAI
Descriptor: 215 EXH VPSR
Value: 0.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R215.EXCFM
Point Name: HU.R215.EXCFM
Point Type: LAO
Descriptor: 215 EXH CFM
Value: 4.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.EXSET
Point Name: HU.R215.EXSET
Point Type: LAO
Descriptor: 215 EXH SET
Value: 4.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.FCFM
Point Name: HU.R215.FCFM
Point Type: LAI
Descriptor: 215 FUME CFM
Value: 491.17
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 11
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R215.FDIFF
Point Name: HU.R215.FDIFF
Point Type: LAO
Descriptor: 215 FLOW DIF
Value: 193.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.MCFM
Point Name: HU.R215.MCFM
Point Type: LAO
Descriptor: 215 CFM MIN
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.MSAIR
Point Name: HU.R215.MSAIR
Point Type: LAO
Descriptor: 215MXSUPAIR
Value: 2040.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.OCC
Point Name: HU.R215.OCC
Point Type: LDO
Descriptor: RM 215 OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R215.OSUP
Point Name: HU.R215.OSUP
Point Type: LAO
Descriptor: 215 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.RHV
Point Name: HU.R215.RHV
Point Type: LAO
Descriptor: 215 RH VALVE
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R215.RM
Point Name: HU.R215.RM
Point Type: LAI
Descriptor: 215 TEMP
Value: 66.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.RMT
Point Name: HU.R215.RMT
Point Type: LAI
Descriptor: 215 TEMP
Value: 66.17
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.RSET
Point Name: HU.R215.RSET
Point Type: LAO
Descriptor: 215 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R215.SACFM
Point Name: HU.R215.SACFM
Point Type: LAO
Descriptor: 215 SUP CFM
Value: 8.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.SASET
Point Name: HU.R215.SASET
Point Type: LAO
Descriptor: 215 SUP SET
Value: 7.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.SBIAS
Point Name: HU.R215.SBIAS
Point Type: LAO
Descriptor: 215 SU BIAS
Value: 7.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.SCFM
Point Name: HU.R215.SCFM
Point Type: LAO
Descriptor: 215 SUP CFM
Value: 788.47
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.SDMP
Point Name: HU.R215.SDMP
Point Type: LAO
Descriptor: 215 SUP DMPR
Value: 6.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R215.SREQ
Point Name: HU.R215.SREQ
Point Type: LAO
Descriptor: 215 SUP REQ
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.SSET
Point Name: HU.R215.SSET
Point Type: LAO
Descriptor: 215 SUP SET
Value: 777.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.SVPRS
Point Name: HU.R215.SVPRS
Point Type: LAI
Descriptor: 215 SUP VPSR
Value: 0.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R215.TEXH
Point Name: HU.R215.TEXH
Point Type: LAO
Descriptor: 215 TOT EXH
Value: 978.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R215.TSUP
Point Name: HU.R215.TSUP
Point Type: LAO
Descriptor: 215 TOT SUP
Value: 792.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.DSET
Point Name: HU.R218.DSET
Point Type: LAO
Descriptor: 218 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.ECFM
Point Name: HU.R218.ECFM
Point Type: LAO
Descriptor: 218 EXH CFM
Value: 418.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.EDMP
Point Name: HU.R218.EDMP
Point Type: LAO
Descriptor: 218 EXH DMPR
Value: 7.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R218.ESET
Point Name: HU.R218.ESET
Point Type: LAO
Descriptor: 218 EXH SET
Value: 413.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.EVPRS
Point Name: HU.R218.EVPRS
Point Type: LAI
Descriptor: 218 EXH VPSR
Value: 0.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R218.EXCFM
Point Name: HU.R218.EXCFM
Point Type: LAO
Descriptor: 218 EXH CFM
Value: 4.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.EXSET
Point Name: HU.R218.EXSET
Point Type: LAO
Descriptor: 218 EXH SET
Value: 4.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.FCFM
Point Name: HU.R218.FCFM
Point Type: LAI
Descriptor: 218 FUME CFM
Value: 553.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.078125
Intercept: -280.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R218.FDIFF
Point Name: HU.R218.FDIFF
Point Type: LAO
Descriptor: 218 FLOW DIF
Value: 198.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.MCFM
Point Name: HU.R218.MCFM
Point Type: LAO
Descriptor: 218 CFM MIN
Value: 494.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.MSAIR
Point Name: HU.R218.MSAIR
Point Type: LAO
Descriptor: BI218MXSUPAR
Value: 1880.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.OCC
Point Name: HU.R218.OCC
Point Type: LDO
Descriptor: RM 218 OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R218.OSUP
Point Name: HU.R218.OSUP
Point Type: LAO
Descriptor: 218 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.RHV
Point Name: HU.R218.RHV
Point Type: LAO
Descriptor: 218 RH VALVE
Value: 8.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R218.RM
Point Name: HU.R218.RM
Point Type: LAI
Descriptor: 218 TEMP
Value: 64.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.3
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.RMT
Point Name: HU.R218.RMT
Point Type: LAI
Descriptor: 218 TEMP
Value: 64.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.3
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.RSET
Point Name: HU.R218.RSET
Point Type: LAO
Descriptor: 218 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R218.SACFM
Point Name: HU.R218.SACFM
Point Type: LAO
Descriptor: 218 SUP CFM
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.SASET
Point Name: HU.R218.SASET
Point Type: LAO
Descriptor: 218 SUP SET
Value: 7.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.SBIAS
Point Name: HU.R218.SBIAS
Point Type: LAO
Descriptor: 218 SU BIAS
Value: 7.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.SCFM
Point Name: HU.R218.SCFM
Point Type: LAO
Descriptor: 218 SUP CFM
Value: 773.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.SDMP
Point Name: HU.R218.SDMP
Point Type: LAO
Descriptor: 218 SUP DMPR
Value: 6.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R218.SREQ
Point Name: HU.R218.SREQ
Point Type: LAO
Descriptor: 218 SUP REQ
Value: 494.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.SSET
Point Name: HU.R218.SSET
Point Type: LAO
Descriptor: 218 SUP SET
Value: 770.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.SVPRS
Point Name: HU.R218.SVPRS
Point Type: LAI
Descriptor: 218 SUP VPSR
Value: 0.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R218.TEXH
Point Name: HU.R218.TEXH
Point Type: LAO
Descriptor: 218 TOT EXH
Value: 965.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R218.TSUP
Point Name: HU.R218.TSUP
Point Type: LAO
Descriptor: 218 TOT SUP
Value: 777.71
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.DRSW
Point Name: HU.R220A.DRSW
Point Type: LDI
Descriptor: 220A DW DRSW
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 08
Normally Closed: No
********************************************************************************
Point System Name: HU.R220A.DSET
Point Name: HU.R220A.DSET
Point Type: LAO
Descriptor: 220A DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.ECFM
Point Name: HU.R220A.ECFM
Point Type: LAO
Descriptor: 220A EXH CFM
Value: 1496.35
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.EDMP
Point Name: HU.R220A.EDMP
Point Type: LAO
Descriptor: 220A EX DMPR
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R220A.ESET
Point Name: HU.R220A.ESET
Point Type: LAO
Descriptor: 220A EXH SET
Value: 2660.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.EVPRS
Point Name: HU.R220A.EVPRS
Point Type: LAI
Descriptor: 220A EX VPSR
Value: 0.26
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 11
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R220A.EXCFM
Point Name: HU.R220A.EXCFM
Point Type: LAO
Descriptor: 220A EXH CFM
Value: 14.83
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.EXSET
Point Name: HU.R220A.EXSET
Point Type: LAO
Descriptor: 220A EXH SET
Value: 26.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.FCFM
Point Name: HU.R220A.FCFM
Point Type: LAI
Descriptor: 220A FUM CFM
Value: 97.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 12
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.023984
Intercept: -146.96001
COV Limit: 10.17588
********************************************************************************
Point System Name: HU.R220A.FDIFF
Point Name: HU.R220A.FDIFF
Point Type: LAO
Descriptor: 220A FLO DIF
Value: 159.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.ISODMP
Point Name: HU.R220A.ISODMP
Point Type: LDO
Descriptor: 220A ISO DPR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 20
Inverted: No
********************************************************************************
Point System Name: HU.R220A.OCC
Point Name: HU.R220A.OCC
Point Type: LDO
Descriptor: RM 220A OCCU
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R220A.OSUP
Point Name: HU.R220A.OSUP
Point Type: LAO
Descriptor: 220A OTHERSU
Value: 428.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.RHV
Point Name: HU.R220A.RHV
Point Type: LAO
Descriptor: 220A RH VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R220A.RM
Point Name: HU.R220A.RM
Point Type: LAI
Descriptor: 220A TEMP
Value: 69.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 10
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.RMT
Point Name: HU.R220A.RMT
Point Type: LAI
Descriptor: 220A TEMP
Value: 69.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 10
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.RSET
Point Name: HU.R220A.RSET
Point Type: LAO
Descriptor: 220A RM SETP
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R220A.SACFM
Point Name: HU.R220A.SACFM
Point Type: LAO
Descriptor: 220A SUP CFM
Value: 13.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.SASET
Point Name: HU.R220A.SASET
Point Type: LAO
Descriptor: 220A SUP SET
Value: 14.21
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.SASHSW
Point Name: HU.R220A.SASHSW
Point Type: LDO
Descriptor: 220A SASH SW
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 21
Inverted: No
********************************************************************************
Point System Name: HU.R220A.SBIAS
Point Name: HU.R220A.SBIAS
Point Type: LAO
Descriptor: 220A SU BIAS
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.SCFM
Point Name: HU.R220A.SCFM
Point Type: LAO
Descriptor: 220A SUP CFM
Value: 975.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.SDMP
Point Name: HU.R220A.SDMP
Point Type: LAO
Descriptor: 220A SU DMPR
Value: 6.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R220A.SSET
Point Name: HU.R220A.SSET
Point Type: LAO
Descriptor: 220A SUP SET
Value: 1449.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.SVPRS
Point Name: HU.R220A.SVPRS
Point Type: LAI
Descriptor: 220A SU VPSR
Value: 0.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: 0 00 09
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R220A.TEXH
Point Name: HU.R220A.TEXH
Point Type: LAO
Descriptor: 220A TOT EXH
Value: 1612.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R220A.TSUP
Point Name: HU.R220A.TSUP
Point Type: LAO
Descriptor: 220A TOT SUP
Value: 1417.81
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM218
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.OCC
Point Name: HU.R2AA.OCC
Point Type: LDO
Descriptor: RM 2AA OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R2AA.OSUP
Point Name: HU.R2AA.OSUP
Point Type: LAO
Descriptor: 2AA OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.RHV
Point Name: HU.R2AA.RHV
Point Type: LAO
Descriptor: 2AA RH VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R2AA.RM
Point Name: HU.R2AA.RM
Point Type: LAI
Descriptor: 2AA TEMP
Value: 68.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.RMT
Point Name: HU.R2AA.RMT
Point Type: LAI
Descriptor: 2AA TEMP
Value: 68.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.RSET
Point Name: HU.R2AA.RSET
Point Type: LAO
Descriptor: 2AA RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R2AA.SACFM
Point Name: HU.R2AA.SACFM
Point Type: LAO
Descriptor: 2AA SUP CFM
Value: 8.64
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.SASET
Point Name: HU.R2AA.SASET
Point Type: LAO
Descriptor: 2AA SUP SET
Value: 10.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.SCFM
Point Name: HU.R2AA.SCFM
Point Type: LAO
Descriptor: 2AA SUP CFM
Value: 859.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.SDMP
Point Name: HU.R2AA.SDMP
Point Type: LAO
Descriptor: 2AA SUP DMPR
Value: 5.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R2AA.SSET
Point Name: HU.R2AA.SSET
Point Type: LAO
Descriptor: 2AA SUP SET
Value: 1095.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AA.SVPRS
Point Name: HU.R2AA.SVPRS
Point Type: LAI
Descriptor: 2AA SUP VPSR
Value: 0.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: 0 00 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R2AA.TSUP
Point Name: HU.R2AA.TSUP
Point Type: LAO
Descriptor: 2AA TOT SUP
Value: 854.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM203
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.OCC
Point Name: HU.R2AD.OCC
Point Type: LDO
Descriptor: RM 2AD OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R2AD.OSUP
Point Name: HU.R2AD.OSUP
Point Type: LAO
Descriptor: 2AD OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.RM
Point Name: HU.R2AD.RM
Point Type: LAI
Descriptor: 2AD TEMP
Value: 69.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.RMT
Point Name: HU.R2AD.RMT
Point Type: LAI
Descriptor: 2AD TEMP
Value: 69.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.RSET
Point Name: HU.R2AD.RSET
Point Type: LAO
Descriptor: 2AD RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R2AD.SACFM
Point Name: HU.R2AD.SACFM
Point Type: LAO
Descriptor: 2AD SUP CFM
Value: 0.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.SASET
Point Name: HU.R2AD.SASET
Point Type: LAO
Descriptor: 2AD SUP SET
Value: 0.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.SCFM
Point Name: HU.R2AD.SCFM
Point Type: LAO
Descriptor: 2AD SUP CFM
Value: 64.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.SDMP
Point Name: HU.R2AD.SDMP
Point Type: LAO
Descriptor: 2AD SUP DMPR
Value: 5.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R2AD.SREQ
Point Name: HU.R2AD.SREQ
Point Type: LAO
Descriptor: 2AD SUP REQ
Value: 66.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AD.SVPRS
Point Name: HU.R2AD.SVPRS
Point Type: LAI
Descriptor: 2AD SUP VPSR
Value: 0.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R2AD.TSUP
Point Name: HU.R2AD.TSUP
Point Type: LAO
Descriptor: 2AD TOT SUP
Value: 66.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM212
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.OCC
Point Name: HU.R2AG.OCC
Point Type: LDO
Descriptor: RM 2AG OCCUP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R2AG.OSUP
Point Name: HU.R2AG.OSUP
Point Type: LAO
Descriptor: 2AG OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.RHV
Point Name: HU.R2AG.RHV
Point Type: LAO
Descriptor: 2AG RH VALVE
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R2AG.RM
Point Name: HU.R2AG.RM
Point Type: LAI
Descriptor: 2AG TEMP
Value: 73.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.RMT
Point Name: HU.R2AG.RMT
Point Type: LAI
Descriptor: 2AG TEMP
Value: 73.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.RSET
Point Name: HU.R2AG.RSET
Point Type: LAO
Descriptor: 2AG RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R2AG.SACFM
Point Name: HU.R2AG.SACFM
Point Type: LAO
Descriptor: 2AG SUP CFM
Value: 1.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.SASET
Point Name: HU.R2AG.SASET
Point Type: LAO
Descriptor: 2AG SUP SET
Value: 1.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.SCFM
Point Name: HU.R2AG.SCFM
Point Type: LAO
Descriptor: 2AG SUP CFM
Value: 180.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.SDMP
Point Name: HU.R2AG.SDMP
Point Type: LAO
Descriptor: 2AG SUP DMPR
Value: 6.91
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R2AG.SSET
Point Name: HU.R2AG.SSET
Point Type: LAO
Descriptor: 2AG SUP SET
Value: 179.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R2AG.SVPRS
Point Name: HU.R2AG.SVPRS
Point Type: LAI
Descriptor: 2AG SUP VPSR
Value: 0.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R2AG.TSUP
Point Name: HU.R2AG.TSUP
Point Type: LAO
Descriptor: 2AG TOT SUP
Value: 181.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM213B
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.DSET
Point Name: HU.R300.DSET
Point Type: LAO
Descriptor: 300 DIF SET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.ECFM
Point Name: HU.R300.ECFM
Point Type: LAO
Descriptor: 300 EXH CFM
Value: 363.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.EDMP
Point Name: HU.R300.EDMP
Point Type: LAO
Descriptor: 300 EXH DMPR
Value: 7.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R300.ESET
Point Name: HU.R300.ESET
Point Type: LAO
Descriptor: 300 EXH SET
Value: 358.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.EVPRS
Point Name: HU.R300.EVPRS
Point Type: LAI
Descriptor: 300 EXH VPSR
Value: 0.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R300.FCFM
Point Name: HU.R300.FCFM
Point Type: LAI
Descriptor: 300 FUME CFM
Value: 127.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 05
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R300.FDIFF
Point Name: HU.R300.FDIFF
Point Type: LAO
Descriptor: 300 FLOW DIF
Value: 69.81
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.MCFM
Point Name: HU.R300.MCFM
Point Type: LAO
Descriptor: 300 CFM MIN
Value: 382.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.MSAIR
Point Name: HU.R300.MSAIR
Point Type: LAO
Descriptor: 300MXSUPAIR
Value: 650.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.OCC
Point Name: HU.R300.OCC
Point Type: LDO
Descriptor: RM 300 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R300.OSUP
Point Name: HU.R300.OSUP
Point Type: LAO
Descriptor: 300 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R300.RHV
Point Name: HU.R300.RHV
Point Type: LAO
Descriptor: 300 RH VALVE
Value: 11.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R300.RM
Point Name: HU.R300.RM
Point Type: LAI
Descriptor: 300 TEMP
Value: 68.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.RMT
Point Name: HU.R300.RMT
Point Type: LAI
Descriptor: 300 TEMP
Value: 68.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.RSET
Point Name: HU.R300.RSET
Point Type: LAO
Descriptor: 300 RM SETPT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R300.SBIAS
Point Name: HU.R300.SBIAS
Point Type: LAO
Descriptor: 300 SU BIAS
Value: 8.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.SCFM
Point Name: HU.R300.SCFM
Point Type: LAO
Descriptor: 300 SUP CFM
Value: 410.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.SDMP
Point Name: HU.R300.SDMP
Point Type: LAO
Descriptor: 300 SUP DMPR
Value: 7.29
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R300.SREQ
Point Name: HU.R300.SREQ
Point Type: LAO
Descriptor: 300 SUP REQ
Value: 410.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.SSET
Point Name: HU.R300.SSET
Point Type: LAO
Descriptor: 300 SUP SET
Value: 414.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.SVPRS
Point Name: HU.R300.SVPRS
Point Type: LAI
Descriptor: 300 SUP VPSR
Value: 0.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R300.TEXH
Point Name: HU.R300.TEXH
Point Type: LAO
Descriptor: 300 TOT EXH
Value: 491.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R300.TSUP
Point Name: HU.R300.TSUP
Point Type: LAO
Descriptor: 300 TOT SUP
Value: 415.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R302.DSET
Point Name: HU.R302.DSET
Point Type: LAO
Descriptor: 302 DIF SET
Value: 200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.ECFM
Point Name: HU.R302.ECFM
Point Type: LAO
Descriptor: 302 EXH CFM
Value: 409.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.EDMP
Point Name: HU.R302.EDMP
Point Type: LAO
Descriptor: 302 EXH DMPR
Value: 6.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R302.ESET
Point Name: HU.R302.ESET
Point Type: LAO
Descriptor: 302 EXH SET
Value: 417.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.EVPRS
Point Name: HU.R302.EVPRS
Point Type: LAI
Descriptor: 302 EXH VPSR
Value: 0.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R302.EXCFM
Point Name: HU.R302.EXCFM
Point Type: LAO
Descriptor: 302 EXH CFM
Value: 4.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R302.EXSET
Point Name: HU.R302.EXSET
Point Type: LAO
Descriptor: 302 EXH SET
Value: 3.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R302.FCFM
Point Name: HU.R302.FCFM
Point Type: LAI
Descriptor: 302 FUME CFM
Value: 484.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R302.FDIFF
Point Name: HU.R302.FDIFF
Point Type: LAO
Descriptor: 302 FLOW DIF
Value: 300.64
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.MCFM
Point Name: HU.R302.MCFM
Point Type: LAO
Descriptor: 302 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.MSAIR
Point Name: HU.R302.MSAIR
Point Type: LAO
Descriptor: 302MXSUPAIR
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.OCC
Point Name: HU.R302.OCC
Point Type: LDO
Descriptor: RM 302 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R302.OSUP
Point Name: HU.R302.OSUP
Point Type: LAO
Descriptor: 302 OTHERSUP
Value: 84.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R302.RHV
Point Name: HU.R302.RHV
Point Type: LAO
Descriptor: 302 RH VALVE
Value: 5.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R302.RM
Point Name: HU.R302.RM
Point Type: LAI
Descriptor: 302 TEMP
Value: 69.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.RMT
Point Name: HU.R302.RMT
Point Type: LAI
Descriptor: 302 TEMP
Value: 69.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.RSET
Point Name: HU.R302.RSET
Point Type: LAO
Descriptor: 302 RM SETPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R302.SACFM
Point Name: HU.R302.SACFM
Point Type: LAO
Descriptor: 302 SUP CFM
Value: 5.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R302.SASET
Point Name: HU.R302.SASET
Point Type: LAO
Descriptor: 302 SUP SET
Value: 6.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R302.SBIAS
Point Name: HU.R302.SBIAS
Point Type: LAO
Descriptor: 302 SU BIAS
Value: 8.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.SCFM
Point Name: HU.R302.SCFM
Point Type: LAO
Descriptor: 302 SUP CFM
Value: 505.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.SDMP
Point Name: HU.R302.SDMP
Point Type: LAO
Descriptor: 302 SUP DMPR
Value: 3.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R302.SNRKSW
Point Name: HU.R302.SNRKSW
Point Type: LDI
Descriptor: SNORKEL SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 14
Normally Closed: No
********************************************************************************
Point System Name: HU.R302.SREQ
Point Name: HU.R302.SREQ
Point Type: LAO
Descriptor: 302 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.SSET
Point Name: HU.R302.SSET
Point Type: LAO
Descriptor: 302 SUP SET
Value: 700.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.SVPRS
Point Name: HU.R302.SVPRS
Point Type: LAI
Descriptor: 302 SUP VPSR
Value: 0.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R302.TEXH
Point Name: HU.R302.TEXH
Point Type: LAO
Descriptor: 302 TOT EXH
Value: 902.81
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R302.TSUP
Point Name: HU.R302.TSUP
Point Type: LAO
Descriptor: 302 TOT SUP
Value: 592.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R307.DSET
Point Name: HU.R307.DSET
Point Type: LAO
Descriptor: 307 DIF SET
Value: 400.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.ECFM
Point Name: HU.R307.ECFM
Point Type: LAO
Descriptor: 307 EXH CFM
Value: 1295.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.EDMP
Point Name: HU.R307.EDMP
Point Type: LAO
Descriptor: 307 EXH DMPR
Value: 7.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R307.ESET
Point Name: HU.R307.ESET
Point Type: LAO
Descriptor: 307 EXH SET
Value: 1271.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.EVPRS
Point Name: HU.R307.EVPRS
Point Type: LAI
Descriptor: 307 EXH VPSR
Value: 0.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R307.FCFM
Point Name: HU.R307.FCFM
Point Type: LAI
Descriptor: 307 FUME CFM
Value: 488.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 04
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R307.FDIFF
Point Name: HU.R307.FDIFF
Point Type: LAO
Descriptor: 307 FLOW DIF
Value: 392.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.MCFM
Point Name: HU.R307.MCFM
Point Type: LAO
Descriptor: 307 MIN CFM
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.MSAIR
Point Name: HU.R307.MSAIR
Point Type: LAO
Descriptor: 307MXSUPAIR
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.OCC
Point Name: HU.R307.OCC
Point Type: LDO
Descriptor: RM 307 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R307.OSUP
Point Name: HU.R307.OSUP
Point Type: LAO
Descriptor: 307 OTHERSUP
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R307.RHV
Point Name: HU.R307.RHV
Point Type: LAO
Descriptor: 307 RH VALVE
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R307.RM
Point Name: HU.R307.RM
Point Type: LAI
Descriptor: 307 TEMP
Value: 71.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.RMT
Point Name: HU.R307.RMT
Point Type: LAI
Descriptor: 307 TEMP
Value: 71.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.RSET
Point Name: HU.R307.RSET
Point Type: LAO
Descriptor: 307 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R307.SBIAS
Point Name: HU.R307.SBIAS
Point Type: LAO
Descriptor: 307 SU BIAS
Value: 8.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.SCFM
Point Name: HU.R307.SCFM
Point Type: LAO
Descriptor: 307 SUP CFM
Value: 1350.29
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.SDMP
Point Name: HU.R307.SDMP
Point Type: LAO
Descriptor: 307 SUP DMPR
Value: 6.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R307.SREQ
Point Name: HU.R307.SREQ
Point Type: LAO
Descriptor: 307 SUP REQ
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.SSET
Point Name: HU.R307.SSET
Point Type: LAO
Descriptor: 307 SUP SET
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.SVPRS
Point Name: HU.R307.SVPRS
Point Type: LAI
Descriptor: 307 SUP VPSR
Value: 0.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R307.TEXH
Point Name: HU.R307.TEXH
Point Type: LAO
Descriptor: 307 TOT EXH
Value: 1777.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R307.TSUP
Point Name: HU.R307.TSUP
Point Type: LAO
Descriptor: 307 TOT SUP
Value: 1332.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM307
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R310.DSET
Point Name: HU.R310.DSET
Point Type: LAO
Descriptor: 310 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.ECFM
Point Name: HU.R310.ECFM
Point Type: LAO
Descriptor: 310 EXH CFM
Value: 516.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.EDMP
Point Name: HU.R310.EDMP
Point Type: LAO
Descriptor: 310 EXH DMPR
Value: 6.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R310.ESET
Point Name: HU.R310.ESET
Point Type: LAO
Descriptor: 310 EXH SET
Value: 509.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.EVPRS
Point Name: HU.R310.EVPRS
Point Type: LAI
Descriptor: 310 EXH VPSR
Value: 0.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R310.EXCFM
Point Name: HU.R310.EXCFM
Point Type: LAO
Descriptor: 310 EXH CFM
Value: 5.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R310.EXSET
Point Name: HU.R310.EXSET
Point Type: LAO
Descriptor: 310 EXH SET
Value: 5.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R310.FCFM
Point Name: HU.R310.FCFM
Point Type: LAI
Descriptor: 310 FUME CFM
Value: 157.91
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 11
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R310.FDIFF
Point Name: HU.R310.FDIFF
Point Type: LAO
Descriptor: 310 FLOW DIF
Value: -6.71
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.MCFM
Point Name: HU.R310.MCFM
Point Type: LAO
Descriptor: 310 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.MSAIR
Point Name: HU.R310.MSAIR
Point Type: LAO
Descriptor: 310MXSUPAIR
Value: 1500.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.OCC
Point Name: HU.R310.OCC
Point Type: LDO
Descriptor: RM 310 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R310.OSUP
Point Name: HU.R310.OSUP
Point Type: LAO
Descriptor: 310 OTHERSUP
Value: 84.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R310.RHV
Point Name: HU.R310.RHV
Point Type: LAO
Descriptor: 310 RH VALVE
Value: 3.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R310.RM
Point Name: HU.R310.RM
Point Type: LAI
Descriptor: 310 TEMP
Value: 70.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.5
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.RMT
Point Name: HU.R310.RMT
Point Type: LAI
Descriptor: 310 TEMP
Value: 70.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.5
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.RSET
Point Name: HU.R310.RSET
Point Type: LAO
Descriptor: 310 RM SETPT
Value: 70.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R310.SACFM
Point Name: HU.R310.SACFM
Point Type: LAO
Descriptor: 310 SUP CFM
Value: 6.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R310.SASET
Point Name: HU.R310.SASET
Point Type: LAO
Descriptor: 310 SUP SET
Value: 6.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R310.SBIAS
Point Name: HU.R310.SBIAS
Point Type: LAO
Descriptor: 310 SU BIAS
Value: 8.91
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.SCFM
Point Name: HU.R310.SCFM
Point Type: LAO
Descriptor: 310 SUP CFM
Value: 596.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.SDMP
Point Name: HU.R310.SDMP
Point Type: LAO
Descriptor: 310 SUP DMPR
Value: 6.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R310.SREQ
Point Name: HU.R310.SREQ
Point Type: LAO
Descriptor: 310 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.SSET
Point Name: HU.R310.SSET
Point Type: LAO
Descriptor: 310 SUP SET
Value: 667.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.SVPRS
Point Name: HU.R310.SVPRS
Point Type: LAI
Descriptor: 310 SUP VPSR
Value: 0.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R310.TEXH
Point Name: HU.R310.TEXH
Point Type: LAO
Descriptor: 310 TOT EXH
Value: 670.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R310.TSUP
Point Name: HU.R310.TSUP
Point Type: LAO
Descriptor: 310 TOT SUP
Value: 660.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM302
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R315.DSET
Point Name: HU.R315.DSET
Point Type: LAO
Descriptor: 315 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.ECFM
Point Name: HU.R315.ECFM
Point Type: LAO
Descriptor: 315 EXH CFM
Value: 499.53
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.EDMP
Point Name: HU.R315.EDMP
Point Type: LAO
Descriptor: 315 EXH DMPR
Value: 6.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R315.ESET
Point Name: HU.R315.ESET
Point Type: LAO
Descriptor: 315 EXH SET
Value: 505.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.EVPRS
Point Name: HU.R315.EVPRS
Point Type: LAI
Descriptor: 315 EXH VPSR
Value: 0.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R315.FCFM
Point Name: HU.R315.FCFM
Point Type: LAI
Descriptor: 315 FUME CFM
Value: 161.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 04
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.018867
Intercept: -67.62
COV Limit: 10.1118
********************************************************************************
Point System Name: HU.R315.FDIFF
Point Name: HU.R315.FDIFF
Point Type: LAO
Descriptor: 315 FLOW DIF
Value: 14.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.MCFM
Point Name: HU.R315.MCFM
Point Type: LAO
Descriptor: 315 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.MSAIR
Point Name: HU.R315.MSAIR
Point Type: LAO
Descriptor: 315MXSUPAIR
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.OCC
Point Name: HU.R315.OCC
Point Type: LDO
Descriptor: RM 315 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R315.OSUP
Point Name: HU.R315.OSUP
Point Type: LAO
Descriptor: 315 OTHERSUP
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R315.RHV
Point Name: HU.R315.RHV
Point Type: LAO
Descriptor: 315 RH VALVE
Value: 3.42
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R315.RM
Point Name: HU.R315.RM
Point Type: LAI
Descriptor: 315 TEMP
Value: 72.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.RMT
Point Name: HU.R315.RMT
Point Type: LAI
Descriptor: 315 TEMP
Value: 72.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.RSET
Point Name: HU.R315.RSET
Point Type: LAO
Descriptor: 315 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R315.SBIAS
Point Name: HU.R315.SBIAS
Point Type: LAO
Descriptor: 315 SU BIAS
Value: 8.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.SCFM
Point Name: HU.R315.SCFM
Point Type: LAO
Descriptor: 315 SUP CFM
Value: 598.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.SDMP
Point Name: HU.R315.SDMP
Point Type: LAO
Descriptor: 315 SUP DMPR
Value: 7.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R315.SREQ
Point Name: HU.R315.SREQ
Point Type: LAO
Descriptor: 315 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.SSET
Point Name: HU.R315.SSET
Point Type: LAO
Descriptor: 315 SUP SET
Value: 666.63
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.SVPRS
Point Name: HU.R315.SVPRS
Point Type: LAI
Descriptor: 315 SUP VPSR
Value: 0.21
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R315.TEXH
Point Name: HU.R315.TEXH
Point Type: LAO
Descriptor: 315 TOT EXH
Value: 663.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R315.TSUP
Point Name: HU.R315.TSUP
Point Type: LAO
Descriptor: 315 TOT SUP
Value: 659.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM315
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R319.DSET
Point Name: HU.R319.DSET
Point Type: LAO
Descriptor: 319 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.ECFM
Point Name: HU.R319.ECFM
Point Type: LAO
Descriptor: 319 EXH CFM
Value: 413.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.EDMP
Point Name: HU.R319.EDMP
Point Type: LAO
Descriptor: 319 EXH DMPR
Value: 7.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R319.ESET
Point Name: HU.R319.ESET
Point Type: LAO
Descriptor: 319 EXH SET
Value: 410.47
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.EVPRS
Point Name: HU.R319.EVPRS
Point Type: LAI
Descriptor: 319 EXH VPSR
Value: 0.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R319.EXCFM
Point Name: HU.R319.EXCFM
Point Type: LAO
Descriptor: 319 EXH CFM
Value: 4.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R319.EXSET
Point Name: HU.R319.EXSET
Point Type: LAO
Descriptor: 319 EXH SET
Value: 4.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R319.FCFM
Point Name: HU.R319.FCFM
Point Type: LAI
Descriptor: 319 FUME CFM
Value: 256.55
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 11
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.018867
Intercept: -67.62
COV Limit: 10.1118
********************************************************************************
Point System Name: HU.R319.FDIFF
Point Name: HU.R319.FDIFF
Point Type: LAO
Descriptor: 319 FLOW DIF
Value: -845.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.MCFM
Point Name: HU.R319.MCFM
Point Type: LAO
Descriptor: 319 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.MSAIR
Point Name: HU.R319.MSAIR
Point Type: LAO
Descriptor: 319MXSUPAIR
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.OCC
Point Name: HU.R319.OCC
Point Type: LDO
Descriptor: RM 319 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R319.OSUP
Point Name: HU.R319.OSUP
Point Type: LAO
Descriptor: 319 OTHERSUP
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R319.RHV
Point Name: HU.R319.RHV
Point Type: LAO
Descriptor: 319 RH VALVE
Value: 6.53
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R319.RM
Point Name: HU.R319.RM
Point Type: LAI
Descriptor: 319 TEMP
Value: 71.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.RMT
Point Name: HU.R319.RMT
Point Type: LAI
Descriptor: 319 TEMP
Value: 71.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.RSET
Point Name: HU.R319.RSET
Point Type: LAO
Descriptor: 319 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R319.SACFM
Point Name: HU.R319.SACFM
Point Type: LAO
Descriptor: 319 SUP CFM
Value: 15.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R319.SASET
Point Name: HU.R319.SASET
Point Type: LAO
Descriptor: 319 SUP SET
Value: 6.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R319.SBIAS
Point Name: HU.R319.SBIAS
Point Type: LAO
Descriptor: 319 SU BIAS
Value: 8.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.SCFM
Point Name: HU.R319.SCFM
Point Type: LAO
Descriptor: 319 SUP CFM
Value: 1454.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.SDMP
Point Name: HU.R319.SDMP
Point Type: LAO
Descriptor: 319 SUP DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R319.SREQ
Point Name: HU.R319.SREQ
Point Type: LAO
Descriptor: 319 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.SSET
Point Name: HU.R319.SSET
Point Type: LAO
Descriptor: 319 SUP SET
Value: 659.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.SVPRS
Point Name: HU.R319.SVPRS
Point Type: LAI
Descriptor: 319 SUP VPSR
Value: 1.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R319.TEXH
Point Name: HU.R319.TEXH
Point Type: LAO
Descriptor: 319 TOT EXH
Value: 663.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R319.TSUP
Point Name: HU.R319.TSUP
Point Type: LAO
Descriptor: 319 TOT SUP
Value: 1514.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R320.DSET
Point Name: HU.R320.DSET
Point Type: LAO
Descriptor: 320 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.ECFM
Point Name: HU.R320.ECFM
Point Type: LAO
Descriptor: 320 EXH CFM
Value: 529.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.EDMP
Point Name: HU.R320.EDMP
Point Type: LAO
Descriptor: 320 EXH DMPR
Value: 7.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.50019
********************************************************************************
Point System Name: HU.R320.ESET
Point Name: HU.R320.ESET
Point Type: LAO
Descriptor: 320 EXH SET
Value: 541.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.EVPRS
Point Name: HU.R320.EVPRS
Point Type: LAI
Descriptor: 320 EXH VPSR
Value: 0.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R320.EXCFM
Point Name: HU.R320.EXCFM
Point Type: LAO
Descriptor: 320 EXH CFM
Value: 5.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.EXSET
Point Name: HU.R320.EXSET
Point Type: LAO
Descriptor: 320 EXH SET
Value: 5.42
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.FCFM
Point Name: HU.R320.FCFM
Point Type: LAI
Descriptor: 320 FUME CFM
Value: 125.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R320.FDIFF
Point Name: HU.R320.FDIFF
Point Type: LAO
Descriptor: 320 FLOW DIF
Value: 93.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.MCFM
Point Name: HU.R320.MCFM
Point Type: LAO
Descriptor: 320 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.MSAIR
Point Name: HU.R320.MSAIR
Point Type: LAO
Descriptor: 326MXSUPAIR
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.OCC
Point Name: HU.R320.OCC
Point Type: LDO
Descriptor: RM 320 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R320.OSUP
Point Name: HU.R320.OSUP
Point Type: LAO
Descriptor: 320 OTHERSUP
Value: 88.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.RHV
Point Name: HU.R320.RHV
Point Type: LAO
Descriptor: 320 RH VALVE
Value: 8.32
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.50019
********************************************************************************
Point System Name: HU.R320.RM
Point Name: HU.R320.RM
Point Type: LAI
Descriptor: 320 TEMP
Value: 71.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.RMT
Point Name: HU.R320.RMT
Point Type: LAI
Descriptor: 320 TEMP
Value: 71.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.RSET
Point Name: HU.R320.RSET
Point Type: LAO
Descriptor: 320 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R320.SACFM
Point Name: HU.R320.SACFM
Point Type: LAO
Descriptor: 320 SUP CFM
Value: 6.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.SASET
Point Name: HU.R320.SASET
Point Type: LAO
Descriptor: 320 SUP SET
Value: 6.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.SBIAS
Point Name: HU.R320.SBIAS
Point Type: LAO
Descriptor: 320 SU BIAS
Value: 6.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.SCFM
Point Name: HU.R320.SCFM
Point Type: LAO
Descriptor: 320 SUP CFM
Value: 567.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.SDMP
Point Name: HU.R320.SDMP
Point Type: LAO
Descriptor: 320 SUP DMPR
Value: 7.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.50019
********************************************************************************
Point System Name: HU.R320.SREQ
Point Name: HU.R320.SREQ
Point Type: LAO
Descriptor: 320 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.SSET
Point Name: HU.R320.SSET
Point Type: LAO
Descriptor: 320 SUP SET
Value: 672.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.SVPRS
Point Name: HU.R320.SVPRS
Point Type: LAI
Descriptor: 320 SUP VPSR
Value: 0.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R320.TEXH
Point Name: HU.R320.TEXH
Point Type: LAO
Descriptor: 320 TOT EXH
Value: 656.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R320.TSUP
Point Name: HU.R320.TSUP
Point Type: LAO
Descriptor: 320 TOT SUP
Value: 654.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.DSET
Point Name: HU.R326.DSET
Point Type: LAO
Descriptor: 326 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.ECFM
Point Name: HU.R326.ECFM
Point Type: LAO
Descriptor: 326 EXH CFM
Value: 511.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.EDMP
Point Name: HU.R326.EDMP
Point Type: LAO
Descriptor: 326 EXH DMPR
Value: 5.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.50019
********************************************************************************
Point System Name: HU.R326.ESET
Point Name: HU.R326.ESET
Point Type: LAO
Descriptor: 326 EXH SET
Value: 540.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.EVPRS
Point Name: HU.R326.EVPRS
Point Type: LAI
Descriptor: 326 EXH VPSR
Value: 0.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R326.EXCFM
Point Name: HU.R326.EXCFM
Point Type: LAO
Descriptor: 326 EXH CFM
Value: 5.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.EXSET
Point Name: HU.R326.EXSET
Point Type: LAO
Descriptor: 326 EXH SET
Value: 5.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.FCFM
Point Name: HU.R326.FCFM
Point Type: LAI
Descriptor: 326 FUME CFM
Value: 126.56
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 11
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R326.FDIFF
Point Name: HU.R326.FDIFF
Point Type: LAO
Descriptor: 326 FLOW DIF
Value: 42.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.MCFM
Point Name: HU.R326.MCFM
Point Type: LAO
Descriptor: 326 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.MSAIR
Point Name: HU.R326.MSAIR
Point Type: LAO
Descriptor: 320MXSUPAIR
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.OCC
Point Name: HU.R326.OCC
Point Type: LDO
Descriptor: RM 326 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R326.OSUP
Point Name: HU.R326.OSUP
Point Type: LAO
Descriptor: 326 OTHERSUP
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.RHV
Point Name: HU.R326.RHV
Point Type: LAO
Descriptor: 326 RH VALVE
Value: 7.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.50019
********************************************************************************
Point System Name: HU.R326.RM
Point Name: HU.R326.RM
Point Type: LAI
Descriptor: 326 TEMP
Value: 72.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.6
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.RMT
Point Name: HU.R326.RMT
Point Type: LAI
Descriptor: 326 TEMP
Value: 72.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.6
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.RSET
Point Name: HU.R326.RSET
Point Type: LAO
Descriptor: 326 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R326.SACFM
Point Name: HU.R326.SACFM
Point Type: LAO
Descriptor: 326 SUP CFM
Value: 6.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.SASET
Point Name: HU.R326.SASET
Point Type: LAO
Descriptor: 326 SUP SET
Value: 6.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.SBIAS
Point Name: HU.R326.SBIAS
Point Type: LAO
Descriptor: 326 SU BIAS
Value: 8.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.SCFM
Point Name: HU.R326.SCFM
Point Type: LAO
Descriptor: 326 SUP CFM
Value: 601.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.SDMP
Point Name: HU.R326.SDMP
Point Type: LAO
Descriptor: 326 SUP DMPR
Value: 7.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.50019
********************************************************************************
Point System Name: HU.R326.SREQ
Point Name: HU.R326.SREQ
Point Type: LAO
Descriptor: 326 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.SSET
Point Name: HU.R326.SSET
Point Type: LAO
Descriptor: 326 SUP SET
Value: 659.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.SVPRS
Point Name: HU.R326.SVPRS
Point Type: LAI
Descriptor: 326 SUP VPSR
Value: 0.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R326.TEXH
Point Name: HU.R326.TEXH
Point Type: LAO
Descriptor: 326 TOT EXH
Value: 658.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R326.TSUP
Point Name: HU.R326.TSUP
Point Type: LAO
Descriptor: 326 TOT SUP
Value: 662.46
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.DSET
Point Name: HU.R327.DSET
Point Type: LAO
Descriptor: 327 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.ECFM
Point Name: HU.R327.ECFM
Point Type: LAO
Descriptor: 327 EXH CFM
Value: 279.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.EDMP
Point Name: HU.R327.EDMP
Point Type: LAO
Descriptor: 327 EXH DMPR
Value: 6.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R327.ESET
Point Name: HU.R327.ESET
Point Type: LAO
Descriptor: 327 EXH SET
Value: 282.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.EVPRS
Point Name: HU.R327.EVPRS
Point Type: LAI
Descriptor: 327 EXH VPSR
Value: 0.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R327.EXCFM
Point Name: HU.R327.EXCFM
Point Type: LAO
Descriptor: 327 EXH CFM
Value: 2.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R327.EXSET
Point Name: HU.R327.EXSET
Point Type: LAO
Descriptor: 327 EXH SET
Value: 2.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R327.FCFM
Point Name: HU.R327.FCFM
Point Type: LAI
Descriptor: 327 FUME CFM
Value: 490.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.018867
Intercept: -67.62
COV Limit: 10.1118
********************************************************************************
Point System Name: HU.R327.FDIFF
Point Name: HU.R327.FDIFF
Point Type: LAO
Descriptor: 327 FLOW DIF
Value: 4.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.MCFM
Point Name: HU.R327.MCFM
Point Type: LAO
Descriptor: 327 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.MSAIR
Point Name: HU.R327.MSAIR
Point Type: LAO
Descriptor: 327MXSUPAIR
Value: 1420.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.OCC
Point Name: HU.R327.OCC
Point Type: LDO
Descriptor: RM 327 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R327.OSUP
Point Name: HU.R327.OSUP
Point Type: LAO
Descriptor: 327 OTHERSUP
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R327.RHV
Point Name: HU.R327.RHV
Point Type: LAO
Descriptor: 327 RH VALVE
Value: 4.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R327.RM
Point Name: HU.R327.RM
Point Type: LAI
Descriptor: 327 TEMP
Value: 72.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.RMT
Point Name: HU.R327.RMT
Point Type: LAI
Descriptor: 327 TEMP
Value: 72.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.RSET
Point Name: HU.R327.RSET
Point Type: LAO
Descriptor: 327 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R327.SACFM
Point Name: HU.R327.SACFM
Point Type: LAO
Descriptor: 327 SUP CFM
Value: 7.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R327.SASET
Point Name: HU.R327.SASET
Point Type: LAO
Descriptor: 327 SUP SET
Value: 7.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.09999
********************************************************************************
Point System Name: HU.R327.SBIAS
Point Name: HU.R327.SBIAS
Point Type: LAO
Descriptor: 327 SU BIAS
Value: 8.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.SCFM
Point Name: HU.R327.SCFM
Point Type: LAO
Descriptor: 327 SUP CFM
Value: 710.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.SDMP
Point Name: HU.R327.SDMP
Point Type: LAO
Descriptor: 327 SUP DMPR
Value: 6.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R327.SREQ
Point Name: HU.R327.SREQ
Point Type: LAO
Descriptor: 327 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.SSET
Point Name: HU.R327.SSET
Point Type: LAO
Descriptor: 327 SUP SET
Value: 766.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.SVPRS
Point Name: HU.R327.SVPRS
Point Type: LAI
Descriptor: 327 SUP VPSR
Value: 0.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R327.TEXH
Point Name: HU.R327.TEXH
Point Type: LAO
Descriptor: 327 TOT EXH
Value: 774.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R327.TSUP
Point Name: HU.R327.TSUP
Point Type: LAO
Descriptor: 327 TOT SUP
Value: 774.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM327
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HU.R329.DSET
Point Name: HU.R329.DSET
Point Type: LAO
Descriptor: 329 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.ECFM
Point Name: HU.R329.ECFM
Point Type: LAO
Descriptor: 329 EXH CFM
Value: 445.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.EDMP
Point Name: HU.R329.EDMP
Point Type: LAO
Descriptor: 329 EXH DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R329.ESET
Point Name: HU.R329.ESET
Point Type: LAO
Descriptor: 329 EXH SET
Value: 108.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.EVPRS
Point Name: HU.R329.EVPRS
Point Type: LAI
Descriptor: 329 EXH VPSR
Value: 1.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 10
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R329.EXCFM
Point Name: HU.R329.EXCFM
Point Type: LAO
Descriptor: 329 EXH CFM
Value: 4.46
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R329.EXSET
Point Name: HU.R329.EXSET
Point Type: LAO
Descriptor: 329 EXH SET
Value: 1.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R329.FCFM
Point Name: HU.R329.FCFM
Point Type: LAI
Descriptor: 329 FUME CFM
Value: 487.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 11
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R329.FDIFF
Point Name: HU.R329.FDIFF
Point Type: LAO
Descriptor: 329 FLOW DIF
Value: 57.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.LOC13
Point Name: HU.R329.LOC13
Point Type: LAO
Descriptor: LOC13
Value: -2.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.LOC8
Point Name: HU.R329.LOC8
Point Type: LAO
Descriptor: LOC8
Value: -2.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.MCFM
Point Name: HU.R329.MCFM
Point Type: LAO
Descriptor: 329 CFM MIN
Value: 397.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.MSAIR
Point Name: HU.R329.MSAIR
Point Type: LAO
Descriptor: 329MXSUPAIR
Value: 800.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.OCC
Point Name: HU.R329.OCC
Point Type: LDO
Descriptor: RM 329 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R329.OSUP
Point Name: HU.R329.OSUP
Point Type: LAO
Descriptor: 329 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.RHV
Point Name: HU.R329.RHV
Point Type: LAO
Descriptor: 329 RH VALVE
Value: 3.21
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R329.RM
Point Name: HU.R329.RM
Point Type: LAI
Descriptor: 329 TEMP
Value: 72.37
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.RMT
Point Name: HU.R329.RMT
Point Type: LAI
Descriptor: 329 TEMP
Value: 72.37
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 09
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.RSET
Point Name: HU.R329.RSET
Point Type: LAO
Descriptor: 329 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R329.SACFM
Point Name: HU.R329.SACFM
Point Type: LAO
Descriptor: 329 SUP CFM
Value: 8.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R329.SASET
Point Name: HU.R329.SASET
Point Type: LAO
Descriptor: 329 SUP SET
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R329.SBIAS
Point Name: HU.R329.SBIAS
Point Type: LAO
Descriptor: 329 SU BIAS
Value: 8.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.SCFM
Point Name: HU.R329.SCFM
Point Type: LAO
Descriptor: 329 SUP CFM
Value: 875.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.SDMP
Point Name: HU.R329.SDMP
Point Type: LAO
Descriptor: 329 SUP DMPR
Value: 14.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R329.SREQ
Point Name: HU.R329.SREQ
Point Type: LAO
Descriptor: 329 SUP REQ
Value: 397.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.SSET
Point Name: HU.R329.SSET
Point Type: LAO
Descriptor: 329 SUP SET
Value: 800.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.SVPRS
Point Name: HU.R329.SVPRS
Point Type: LAI
Descriptor: 329 SUP VPSR
Value: 1.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R329.TEXH
Point Name: HU.R329.TEXH
Point Type: LAO
Descriptor: 329 TOT EXH
Value: 933.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R329.TSUP
Point Name: HU.R329.TSUP
Point Type: LAO
Descriptor: 329 TOT SUP
Value: 875.31
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.DSET
Point Name: HU.R334.DSET
Point Type: LAO
Descriptor: 334 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.ECFM
Point Name: HU.R334.ECFM
Point Type: LAO
Descriptor: 334 EXH CFM
Value: 538.53
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.EDMP
Point Name: HU.R334.EDMP
Point Type: LAO
Descriptor: 334 EXH DMPR
Value: 6.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R334.ESET
Point Name: HU.R334.ESET
Point Type: LAO
Descriptor: 334 EXH SET
Value: 540.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.EVPRS
Point Name: HU.R334.EVPRS
Point Type: LAI
Descriptor: 334 EXH VPSR
Value: 0.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R334.EXCFM
Point Name: HU.R334.EXCFM
Point Type: LAO
Descriptor: 334 EXH CFM
Value: 5.43
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R334.EXSET
Point Name: HU.R334.EXSET
Point Type: LAO
Descriptor: 334 EXH SET
Value: 5.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R334.FCFM
Point Name: HU.R334.FCFM
Point Type: LAI
Descriptor: 334 FUME CFM
Value: 126.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 07
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.020938
Intercept: -129.03999
COV Limit: 10.11455
********************************************************************************
Point System Name: HU.R334.FDIFF
Point Name: HU.R334.FDIFF
Point Type: LAO
Descriptor: 334 FLOW DIF
Value: 52.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.MCFM
Point Name: HU.R334.MCFM
Point Type: LAO
Descriptor: 334 CFM MIN
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.MSAIR
Point Name: HU.R334.MSAIR
Point Type: LAO
Descriptor: 334MXSUPAIR
Value: 1500.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.OCC
Point Name: HU.R334.OCC
Point Type: LDO
Descriptor: RM 334 OCCUP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.R334.OSUP
Point Name: HU.R334.OSUP
Point Type: LAO
Descriptor: 334 OTHERSUP
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.RHV
Point Name: HU.R334.RHV
Point Type: LAO
Descriptor: 334 RH VALVE
Value: 8.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R334.RM
Point Name: HU.R334.RM
Point Type: LAI
Descriptor: 334 TEMP
Value: 72.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.RMT
Point Name: HU.R334.RMT
Point Type: LAI
Descriptor: 334 TEMP
Value: 72.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.RSET
Point Name: HU.R334.RSET
Point Type: LAO
Descriptor: 334 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R334.SACFM
Point Name: HU.R334.SACFM
Point Type: LAO
Descriptor: 334 SUP CFM
Value: 6.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R334.SASET
Point Name: HU.R334.SASET
Point Type: LAO
Descriptor: 334 SUP SET
Value: 6.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.00999
********************************************************************************
Point System Name: HU.R334.SBIAS
Point Name: HU.R334.SBIAS
Point Type: LAO
Descriptor: 334 SU BIAS
Value: 9.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.SCFM
Point Name: HU.R334.SCFM
Point Type: LAO
Descriptor: 334 SUP CFM
Value: 596.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.SDMP
Point Name: HU.R334.SDMP
Point Type: LAO
Descriptor: 334 SUP DMPR
Value: 6.71
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R334.SREQ
Point Name: HU.R334.SREQ
Point Type: LAO
Descriptor: 334 SUP REQ
Value: 667.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.SSET
Point Name: HU.R334.SSET
Point Type: LAO
Descriptor: 334 SUP SET
Value: 654.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.SVPRS
Point Name: HU.R334.SVPRS
Point Type: LAI
Descriptor: 334 SUP VPSR
Value: 0.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.R334.TEXH
Point Name: HU.R334.TEXH
Point Type: LAO
Descriptor: 334 TOT EXH
Value: 660.83
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R334.TSUP
Point Name: HU.R334.TSUP
Point Type: LAO
Descriptor: 334 TOT SUP
Value: 684.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R3AA.RM
Point Name: HU.R3AA.RM
Point Type: LAI
Descriptor: 3AA TEMP
Value: 71.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R3AA.RMT
Point Name: HU.R3AA.RMT
Point Type: LAI
Descriptor: 3AA TEMP
Value: 71.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R3AA.RSET
Point Name: HU.R3AA.RSET
Point Type: LAO
Descriptor: 3AA RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.R3AA.SCFM
Point Name: HU.R3AA.SCFM
Point Type: LAO
Descriptor: 3AA SUP CFM
Value: 44.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R3AA.SDMP
Point Name: HU.R3AA.SDMP
Point Type: LAO
Descriptor: 3AA SUP DMPR
Value: 8.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 1.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.R3AA.SSET
Point Name: HU.R3AA.SSET
Point Type: LAO
Descriptor: 3AA SUP SET
Value: 45.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.R3AA.SVPRS
Point Name: HU.R3AA.SVPRS
Point Type: LAI
Descriptor: 3AA SUP VPSR
Value: 0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.RB02.DSET
Point Name: HU.RB02.DSET
Point Type: LAO
Descriptor: B02 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.ECAL
Point Name: HU.RB02.ECAL
Point Type: LAO
Descriptor: B02 CAL EXH
Value: 0.45
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.EDMP
Point Name: HU.RB02.EDMP
Point Type: LAO
Descriptor: B02 EXH DMPR
Value: 6.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.RB02.ESET
Point Name: HU.RB02.ESET
Point Type: LAO
Descriptor: B02 EXH SET
Value: 0.49
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.EVPRS
Point Name: HU.RB02.EVPRS
Point Type: LAI
Descriptor: B02 EXH VPSR
Value: 0.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.RB02.EXCFM
Point Name: HU.RB02.EXCFM
Point Type: LAO
Descriptor: B02 EXH CFM
Value: 48.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.EXSET
Point Name: HU.RB02.EXSET
Point Type: LAO
Descriptor: B02 EXH SET
Value: 49.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.FCFM
Point Name: HU.RB02.FCFM
Point Type: LAI
Descriptor: B02 FUME CFM
Value: 414.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 09
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.033789
Intercept: -208.10001
COV Limit: 4.84944
********************************************************************************
Point System Name: HU.RB02.FDIFF
Point Name: HU.RB02.FDIFF
Point Type: LAO
Descriptor: B02 FLOW DIF
Value: -1.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.MNCFM
Point Name: HU.RB02.MNCFM
Point Type: LAO
Descriptor: B02 CFM MIN
Value: 195.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.MXSA
Point Name: HU.RB02.MXSA
Point Type: LAO
Descriptor: B02MXSUPAIR
Value: 680.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.OCC
Point Name: HU.RB02.OCC
Point Type: LDO
Descriptor: B02 OCCUPIED
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.RB02.OSUP
Point Name: HU.RB02.OSUP
Point Type: LAO
Descriptor: B02 OTHERSUP
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.RHV
Point Name: HU.RB02.RHV
Point Type: LAO
Descriptor: B02 RH VALVE
Value: 7.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.RB02.RM
Point Name: HU.RB02.RM
Point Type: LAI
Descriptor: B02 TEMP
Value: 70.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.RMT
Point Name: HU.RB02.RMT
Point Type: LAI
Descriptor: B02 TEMP
Value: 70.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.RSET
Point Name: HU.RB02.RSET
Point Type: LAO
Descriptor: B02 RM SETPT
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.RB02.SASET
Point Name: HU.RB02.SASET
Point Type: LAO
Descriptor: B02 SUP SET
Value: 4.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.SBIAS
Point Name: HU.RB02.SBIAS
Point Type: LAO
Descriptor: B02 SUP BIAS
Value: 8.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.SCAL
Point Name: HU.RB02.SCAL
Point Type: LAO
Descriptor: B02 CAL SUP
Value: 4.63
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.SCFM
Point Name: HU.RB02.SCFM
Point Type: LAO
Descriptor: B02 SUP CFM
Value: 463.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.SDMP
Point Name: HU.RB02.SDMP
Point Type: LAO
Descriptor: B02 SUP DMPR
Value: 6.29
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 19
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.RB02.SREQ
Point Name: HU.RB02.SREQ
Point Type: LAO
Descriptor: B02 SUP REQ
Value: 195.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.SSET
Point Name: HU.RB02.SSET
Point Type: LAO
Descriptor: B02 SUP SET
Value: 465.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.SVPRS
Point Name: HU.RB02.SVPRS
Point Type: LAI
Descriptor: B02 SUP VPSR
Value: 0.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.RB02.TEXH
Point Name: HU.RB02.TEXH
Point Type: LAO
Descriptor: B02 TOT EXH
Value: 465.91
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.TEXHI
Point Name: HU.RB02.TEXHI
Point Type: LDI
Descriptor: BO2 TABLE EXH
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 12
Normally Closed: No
********************************************************************************
Point System Name: HU.RB02.TEXHO
Point Name: HU.RB02.TEXHO
Point Type: LAO
Descriptor: B02 TABLE EXH
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02.TSUP
Point Name: HU.RB02.TSUP
Point Type: LAO
Descriptor: B02 TOT SUP
Value: 471.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.DSET
Point Name: HU.RB02A.DSET
Point Type: LAO
Descriptor: B02A DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.FCFM
Point Name: HU.RB02A.FCFM
Point Type: LAI
Descriptor: B02A FUM CFM
Value: 405.08
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 03
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.033789
Intercept: -208.10001
COV Limit: 9.976
********************************************************************************
Point System Name: HU.RB02A.FDIFF
Point Name: HU.RB02A.FDIFF
Point Type: LAO
Descriptor: B02A FLW DIF
Value: -96.21
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.OCC
Point Name: HU.RB02A.OCC
Point Type: LDO
Descriptor: B02A OCCUPIE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.RB02A.RHV
Point Name: HU.RB02A.RHV
Point Type: LAO
Descriptor: B02A RH VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.RB02A.RMT
Point Name: HU.RB02A.RMT
Point Type: LAI
Descriptor: B02A TEMP
Value: 70.41
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.RSET
Point Name: HU.RB02A.RSET
Point Type: LAO
Descriptor: B02A RM STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.RB02A.SASET
Point Name: HU.RB02A.SASET
Point Type: LAO
Descriptor: B02A SUP SET
Value: 4.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.SBIAS
Point Name: HU.RB02A.SBIAS
Point Type: LAO
Descriptor: B02A SU BIAS
Value: 7.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.SCAL
Point Name: HU.RB02A.SCAL
Point Type: LAO
Descriptor: B02A CAL SUP
Value: 4.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.SCFM
Point Name: HU.RB02A.SCFM
Point Type: LAO
Descriptor: B02A SUP CFM
Value: 495.46
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.SDMP
Point Name: HU.RB02A.SDMP
Point Type: LAO
Descriptor: B02A SU DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.RB02A.SSET
Point Name: HU.RB02A.SSET
Point Type: LAO
Descriptor: B02A SUP SET
Value: 405.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB02A.SVPRS
Point Name: HU.RB02A.SVPRS
Point Type: LAI
Descriptor: B02A SU VPSR
Value: 0.65
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB02
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HU.RB03.DSET
Point Name: HU.RB03.DSET
Point Type: LAO
Descriptor: B03 DIF SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.FCFM
Point Name: HU.RB03.FCFM
Point Type: LAI
Descriptor: B03 FUME CFM
Value: 203.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: 0 00 03
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.033693
Intercept: -207.45415
COV Limit: 4.90339
********************************************************************************
Point System Name: HU.RB03.FDIFF
Point Name: HU.RB03.FDIFF
Point Type: LAO
Descriptor: B03 FLOW DIF
Value: -11.49
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.OCC
Point Name: HU.RB03.OCC
Point Type: LDO
Descriptor: B03 OCCUPIED
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
********************************************************************************
Point System Name: HU.RB03.RHV
Point Name: HU.RB03.RHV
Point Type: LAO
Descriptor: B03 RH VALVE
Value: 5.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: 0 00 18
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.RB03.RM
Point Name: HU.RB03.RM
Point Type: LAI
Descriptor: B03 TEMP
Value: 72.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.RMT
Point Name: HU.RB03.RMT
Point Type: LAI
Descriptor: B03 TEMP
Value: 72.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: 0 00 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.7
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.RSET
Point Name: HU.RB03.RSET
Point Type: LAO
Descriptor: B03 RM SETPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: HU.RB03.SASET
Point Name: HU.RB03.SASET
Point Type: LAO
Descriptor: B03 SUP SET
Value: 2.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.SBIAS
Point Name: HU.RB03.SBIAS
Point Type: LAO
Descriptor: B03 SUP BIAS
Value: 9.58
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.SCAL
Point Name: HU.RB03.SCAL
Point Type: LAO
Descriptor: B03 CAL SUP
Value: 2.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: C CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.SCFM
Point Name: HU.RB03.SCFM
Point Type: LAO
Descriptor: B03 SUP CFM
Value: 205.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.SDMP
Point Name: HU.RB03.SDMP
Point Type: LAO
Descriptor: B03 SUP DMPR
Value: 7.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: 0 00 17
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.49938
********************************************************************************
Point System Name: HU.RB03.SSET
Point Name: HU.RB03.SSET
Point Type: LAO
Descriptor: B03 SUP SET
Value: 203.26
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HU.RB03.SVPRS
Point Name: HU.RB03.SVPRS
Point Type: LAI
Descriptor: B03 SUP VPSR
Value: 0.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RMB03
Point Address: 0 00 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000041
Intercept: -0.25022
COV Limit: 0.09993
********************************************************************************
Point System Name: HUL111A
Point Name: HUL111A
Point Type: LDI
Descriptor: HD 111A ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 1 05 07
Normally Closed: No
********************************************************************************
Point System Name: HULINGS.300.BLAST.FRZ.ALARM
Point Name: HULINGS.300.BLAST.FRZ.ALARM
Point Type: LDO
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: SS.PXCM03
Point Address: -Virtual-
********************************************************************************
Point System Name: HULINGS.322.BLAST.FRZ.ALARM
Point Name: HULINGS.322.BLAST.FRZ.ALARM
Point Type: LDO
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: SS.PXCM03
Point Address: -Virtual-
********************************************************************************
Point System Name: HULINGS.329.BLAST.FRZ.ALARM
Point Name: HULINGS.329.BLAST.FRZ.ALARM
Point Type: LDO
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: SS.PXCM03
Point Address: -Virtual-
********************************************************************************
Point System Name: HULINGS.BLAST.FRZ.300.ALM
Point Name: HULINGS.BLAST.FRZ.300.ALM
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM301
Point Address: 0 00 09
Normally Closed: No
********************************************************************************
Point System Name: HULINGS.BLAST.FRZ.322.ALM
Point Name: HULINGS.BLAST.FRZ.322.ALM
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM334
Point Address: 0 00 12
Normally Closed: No
********************************************************************************
Point System Name: HULINGS.BLAST.FRZ.329.ALM
Point Name: HULINGS.BLAST.FRZ.329.ALM
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.RM320
Point Address: 0 00 12
Normally Closed: No
********************************************************************************
Point System Name: HULINGS.COND
Point Name: HULINGS.COND
Point Type: LPACI
Descriptor: HULINGS COND MTR
Value: 607150.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 04 05
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
********************************************************************************
Point System Name: HULINGS.COND.METER
Point Name: HULINGS.COND.METER
Point Type: LPACI
Descriptor: HULING CONDENSAT
Value: 465020.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 04 05
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
********************************************************************************
Point System Name: HULINGS.E.TEST
Point Name: HULINGS.E.TEST
Point Type: LPACI
Descriptor:
Value: 1179096.875
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 12 01
Gain: 0.8
Count Both Edges: No
COV Limit: 0.8
********************************************************************************
Point System Name: HULINGS.ELEC
Point Name: HULINGS.ELEC
Point Type: LPACI
Descriptor: LPACI
Value: 1920296.625
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: KWH
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 12 01
Gain: 0.8
Count Both Edges: No
COV Limit: 2.0
********************************************************************************
Point System Name: HULINGS.ELEC.DEMAND
Point Name: HULINGS.ELEC.DEMAND
Point Type: LAO
Descriptor: ELECTRIC DEMAND
Value: 174.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.ELEC.HOLDER
Point Name: HULINGS.ELEC.HOLDER
Point Type: LAO
Descriptor:
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.ELEC.LPACI
Point Name: HULINGS.ELEC.LPACI
Point Type: LAO
Descriptor: ELECTRIC DEMAND
Value: 412.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.ELEC.METER.READING
Point Name: HULINGS.ELEC.METER.READING
Point Type: LPACI
Descriptor:
Value: 1839056.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Gain: 0.0
Count Both Edges: No
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.FIRE
Point Name: HULINGS.FIRE
Point Type: LDI
Descriptor: FIRE ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 03
Normally Closed: No
********************************************************************************
Point System Name: HULINGS.H2O.METER.READING
Point Name: HULINGS.H2O.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 726711104
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: HULINGS.LAST.MONTH.ELEC.CONSUM
Point Name: HULINGS.LAST.MONTH.ELEC.CONSUM
Point Type: LAO
Descriptor: LAST MNTH CONSMP
Value: 109831.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.LAST.MONTH.H2O.CONSUMP
Point Name: HULINGS.LAST.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST MNTH CONSMP
Value: 64704
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.LAST.MONTH.STEAM.CONSU
Point Name: HULINGS.LAST.MONTH.STEAM.CONSU
Point Type: LAO
Descriptor: LAST MONTH STEAM
Value: 4773761.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: HULINGS.LAST.WEEK.ELEC.CONSUMP
Point Name: HULINGS.LAST.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 28235.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.LAST.WEEK.H2O.CONSUMP
Point Name: HULINGS.LAST.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 16448
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.LAST.WEEK.STEAM.CONSU
Point Name: HULINGS.LAST.WEEK.STEAM.CONSU
Point Type: LAO
Descriptor: LAST WEEK STEAM
Value: 1120236.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: HULINGS.MONTH.ELEC.CONSUMP
Point Name: HULINGS.MONTH.ELEC.CONSUMP
Point Type: LAO
Descriptor: THIS MNTH CONSMP
Value: 59400.88
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.MONTH.H2O.CONSUMP
Point Name: HULINGS.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: THIS MNTH CONSMP
Value: 33088
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.MONTH.STEAM.CONSUMP
Point Name: HULINGS.MONTH.STEAM.CONSUMP
Point Type: LAO
Descriptor: MONTH STEAM
Value: 2392824.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: HULINGS.STEAM.DEMAND
Point Name: HULINGS.STEAM.DEMAND
Point Type: LAI
Descriptor: STEAM DEMAND
Value: 6616.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM/HR
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM30
Point Address: 0 08 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 1.074219
Intercept: 0.0
COV Limit: 50.0
********************************************************************************
Point System Name: HULINGS.TODAY.ELEC.CONSUMP
Point Name: HULINGS.TODAY.ELEC.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 2448.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.TODAY.H2O.CONSUMP
Point Name: HULINGS.TODAY.H2O.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 896
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.TODAY.STEAM.CONSUMP
Point Name: HULINGS.TODAY.STEAM.CONSUMP
Point Type: LAO
Descriptor: TODAY STEAM
Value: 11181.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: HULINGS.TUNNEL
Point Name: HULINGS.TUNNEL
Point Type: LDI
Descriptor: DOOR ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 02
Normally Closed: Yes
********************************************************************************
Point System Name: HULINGS.WATER.DEMAND
Point Name: HULINGS.WATER.DEMAND
Point Type: LAO
Descriptor: HULING H2O DEMND
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.WATER.HI
Point Name: HULINGS.WATER.HI
Point Type: LPACI
Descriptor: LPACI
Value: 695585088.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 12 03
Gain: 100.0
Count Both Edges: No
COV Limit: 100.0
********************************************************************************
Point System Name: HULINGS.WATER.HIGH
Point Name: HULINGS.WATER.HIGH
Point Type: LAO
Descriptor: PDL WATER HIGH
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.WATER.LO
Point Name: HULINGS.WATER.LO
Point Type: LPACI
Descriptor: LPACI
Value: 31126030.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 12 04
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
********************************************************************************
Point System Name: HULINGS.WATER.LOW
Point Name: HULINGS.WATER.LOW
Point Type: LAO
Descriptor: PDL WATER LOW
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.WEEK.ELEC.CONSUMP
Point Name: HULINGS.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.WEEK.H2O.CONSUMP
Point Name: HULINGS.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.WEEK.STEAM.CONSUMP
Point Name: HULINGS.WEEK.STEAM.CONSUMP
Point Type: LAO
Descriptor: WEEK STEAM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: HULINGS.YEST.ELEC.CONSUMP
Point Name: HULINGS.YEST.ELEC.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 3853.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.YEST.H2O.CONSUMP
Point Name: HULINGS.YEST.H2O.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 448
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: HULINGS.YEST.STEAM.CONSUMP
Point Name: HULINGS.YEST.STEAM.CONSUMP
Point Type: LAO
Descriptor: YEST STEAM
Value: 158877.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: BI.LAB.HW.TEMP
Point Name: BI.LAB.HW.TEMP
Point Type: LAI
Descriptor: LAB HOT H2O TEMP
Value: 149.37
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 200.0
Low Limit: 95.0
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.008952
Intercept: -25.00011
COV Limit: 0.5
********************************************************************************
Point System Name: BI.LAB.HW.VLV
Point Name: BI.LAB.HW.VLV
Point Type: LAO
Descriptor: LAB HOT H2O VLV
Value: 6.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: BI.LAB.HWEN
Point Name: BI.LAB.HWEN
Point Type: LDO
Descriptor: LAB HW ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BI.LAB.HWSP
Point Name: BI.LAB.HWSP
Point Type: LAO
Descriptor: DOM H2O STPT
Value: 150.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI102M
Point Name: BI102M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 920.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI121BM
Point Name: BI121BM
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1235.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI121M
Point Name: BI121M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1485.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI1BRL
Point Name: BI1BRL
Point Type: LDO
Descriptor: BYPAS ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BI1CCT
Point Name: BI1CCT
Point Type: LAI
Descriptor: A1 CCL TEMP
Value: 50.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -5.00013
COV Limit: 0.996
********************************************************************************
Point System Name: BI1CCV
Point Name: BI1CCV
Point Type: LAO
Descriptor: A1 CCOIL VLV
Value: 9.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BI1CFM
Point Name: BI1CFM
Point Type: LAO
Descriptor: AH2 AIR VOLU
Value: 8565.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 200.0
********************************************************************************
Point System Name: BI1DSC
Point Name: BI1DSC
Point Type: LAO
Descriptor: STATIC SET
Value: 1.5
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BI1DSP
Point Name: BI1DSP
Point Type: LAI
Descriptor: A1 SA STATIC
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BI1FFP
Point Name: BI1FFP
Point Type: LDI
Descriptor: A1 FNL FLTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 03
Normally Closed: No
********************************************************************************
Point System Name: BI1FRZ
Point Name: BI1FRZ
Point Type: LDI
Descriptor: A1 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 04
Normally Closed: No
********************************************************************************
Point System Name: BI1HMC
Point Name: BI1HMC
Point Type: LAO
Descriptor: ZONE HUM SET
Value: 35.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI1HME
Point Name: BI1HME
Point Type: LDO
Descriptor: A1 HUM ENA
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 05 02
Inverted: No
********************************************************************************
Point System Name: BI1HMV
Point Name: BI1HMV
Point Type: LAO
Descriptor: A1 HUM VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI1HRC
Point Name: BI1HRC
Point Type: LAO
Descriptor: HR SUP TEMP
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI1HRT
Point Name: BI1HRT
Point Type: LAI
Descriptor: A1 HTREC TMP
Value: 67.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI1HRV
Point Name: BI1HRV
Point Type: LAO
Descriptor: A1 HREC VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI1HSP
Point Name: BI1HSP
Point Type: LDO
Descriptor: HIGH STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BI1HT1
Point Name: BI1HT1
Point Type: LAI
Descriptor: A1 HC1 TEMP
Value: 66.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI1HT2
Point Name: BI1HT2
Point Type: LAI
Descriptor: A1 HC2 TEMP
Value: 66.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.54
COV Limit: 0.996
********************************************************************************
Point System Name: BI1HV1
Point Name: BI1HV1
Point Type: LAO
Descriptor: A1 HT VLV1
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI1HV2
Point Name: BI1HV2
Point Type: LAO
Descriptor: A1 HT VLV2
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI1OCC
Point Name: BI1OCC
Point Type: LDO
Descriptor: OCCUPIED ENA
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BI1PFP
Point Name: BI1PFP
Point Type: LDI
Descriptor: A1 PRE FLTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 02
Normally Closed: No
********************************************************************************
Point System Name: BI1PHT
Point Name: BI1PHT
Point Type: LAI
Descriptor: A1 PHT TEMP
Value: 68.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI1PHV
Point Name: BI1PHV
Point Type: LAO
Descriptor: A1 PHT VLV
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 04 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI1RHS
Point Name: BI1RHS
Point Type: LAO
Descriptor: REHEAT SET
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI1RRC
Point Name: BI1RRC
Point Type: LAO
Descriptor: HT REC RET T
Value: 32.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI1RRT
Point Name: BI1RRT
Point Type: LAI
Descriptor: A1 HREC RTMP
Value: 74.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI1SAC
Point Name: BI1SAC
Point Type: LAO
Descriptor: SUP AIR SET
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI1SAT
Point Name: BI1SAT
Point Type: LAI
Descriptor: A1 SA TEMP
Value: 55.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 75.0
Low Limit: 50.0
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 1.0
********************************************************************************
Point System Name: BI1SAV
Point Name: BI1SAV
Point Type: LAI
Descriptor: A1 VEL PRESS
Value: 148.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UINH2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.020345
Intercept: -124.99928
COV Limit: 0.99608
********************************************************************************
Point System Name: BI1SS
Point Name: BI1SS
Point Type: L2SL
Descriptor: A1 STRT STOP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 05 01
Inverted: No
Proof Point Address: 0 01 01
Normally Closed: No
Proof Delay: 40 Informational Text
********************************************************************************
Point System Name: BI1SSP
Point Name: BI1SSP
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BI1SSR
Point Name: BI1SSR
Point Type: LDO
Descriptor: A1 EMG RUN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 05 04
Inverted: No
********************************************************************************
Point System Name: BI1SSS
Point Name: BI1SSS
Point Type: LDO
Descriptor: A1 EMG STOP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 05 03
Inverted: No
********************************************************************************
Point System Name: BI1VRL
Point Name: BI1VRL
Point Type: LDO
Descriptor: VFD ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BI1VRL.IN.OPERATOR
Point Name: BI1VRL.IN.OPERATOR
Point Type: LDO
Descriptor: VFD ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BI1Z1T
Point Name: BI1Z1T
Point Type: LAI
Descriptor: BO1 TEMP
Value: 70.46
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI1Z2T
Point Name: BI1Z2T
Point Type: LAI
Descriptor: B03B TEMP
Value: 72.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI1Z3T
Point Name: BI1Z3T
Point Type: LAI
Descriptor: B23 TEMP
Value: 69.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 80.04
Low Limit: 65.02
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -3.46
COV Limit: 0.51792
********************************************************************************
Point System Name: BI1Z4T
Point Name: BI1Z4T
Point Type: LAI
Descriptor: B33 TEMP
Value: 76.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 85.0
Low Limit: 70.0
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 1.0
********************************************************************************
Point System Name: BI1ZAH
Point Name: BI1ZAH
Point Type: LAI
Descriptor: RM BCE HUMID
Value: 31.59
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 03 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -23.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BI202M
Point Name: BI202M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1260.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI203AM
Point Name: BI203AM
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1452.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI203M
Point Name: BI203M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1683.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI206M
Point Name: BI206M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1270.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI213BM
Point Name: BI213BM
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 680.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI213M
Point Name: BI213M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1440.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI215M
Point Name: BI215M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 2040.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI218M
Point Name: BI218M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1880.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI2CCT
Point Name: BI2CCT
Point Type: LAI
Descriptor: A2 CCL TEMP
Value: 52.64
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2CCV
Point Name: BI2CCV
Point Type: LAO
Descriptor: A2 CCOIL VLV
Value: 5.42
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI2CFM
Point Name: BI2CFM
Point Type: LAO
Descriptor: AH2 AIR VOLU
Value: 17701.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 500.0
********************************************************************************
Point System Name: BI2DSC
Point Name: BI2DSC
Point Type: LAO
Descriptor: STATIC SET
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BI2DSP
Point Name: BI2DSP
Point Type: LAI
Descriptor: A2 SA STATIC
Value: 1.49
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 03 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.54909
COV Limit: 0.10003
********************************************************************************
Point System Name: BI2FFP
Point Name: BI2FFP
Point Type: LDI
Descriptor: A2 FNL FLTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 01 03
Normally Closed: No
********************************************************************************
Point System Name: BI2FRZ
Point Name: BI2FRZ
Point Type: LDI
Descriptor: A2 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 01 04
Normally Closed: No
********************************************************************************
Point System Name: BI2HMC
Point Name: BI2HMC
Point Type: LAO
Descriptor: ZONE HUM SET
Value: 30.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI2HME
Point Name: BI2HME
Point Type: LDO
Descriptor: A2 HUM ENA
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 06 02
Inverted: No
********************************************************************************
Point System Name: BI2HMV
Point Name: BI2HMV
Point Type: LAO
Descriptor: A2 HUM VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI2HRC
Point Name: BI2HRC
Point Type: LAO
Descriptor: HR SUP TEMP
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI2HRT
Point Name: BI2HRT
Point Type: LAI
Descriptor: A2 HTREC TMP
Value: 65.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2HRV
Point Name: BI2HRV
Point Type: LAO
Descriptor: A2 HREC VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI2HSP
Point Name: BI2HSP
Point Type: LDO
Descriptor: HIGH STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BI2HT1
Point Name: BI2HT1
Point Type: LAI
Descriptor: A2 HC1 TEMP
Value: 67.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 3.67501
COV Limit: 0.996
********************************************************************************
Point System Name: BI2HT2
Point Name: BI2HT2
Point Type: LAI
Descriptor: A2 HC2 TEMP
Value: 65.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.54
COV Limit: 0.996
********************************************************************************
Point System Name: BI2HV1
Point Name: BI2HV1
Point Type: LAO
Descriptor: A2 HT VLV1
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI2HV2
Point Name: BI2HV2
Point Type: LAO
Descriptor: A2 HT VLV2
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI2OCC
Point Name: BI2OCC
Point Type: LDO
Descriptor: OCCUPIED ENA
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BI2PFP
Point Name: BI2PFP
Point Type: LDI
Descriptor: A2 FRE FLTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 01 02
Normally Closed: No
********************************************************************************
Point System Name: BI2PHT
Point Name: BI2PHT
Point Type: LAI
Descriptor: A2 PHT TEMP
Value: 65.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2PHV
Point Name: BI2PHV
Point Type: LAO
Descriptor: A2 PHT VLV
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI2RRC
Point Name: BI2RRC
Point Type: LAO
Descriptor: HT REC RET T
Value: 32.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI2RRT
Point Name: BI2RRT
Point Type: LAI
Descriptor: A2 HREC RTMP
Value: 72.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2SAC
Point Name: BI2SAC
Point Type: LAO
Descriptor: SUP AIR SET
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI2SAT
Point Name: BI2SAT
Point Type: LAI
Descriptor: A2 SA TEMP
Value: 54.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2SAV
Point Name: BI2SAV
Point Type: LAI
Descriptor: A2 VEL PRESS
Value: 52.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UINH2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 03 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.020345
Intercept: -124.99928
COV Limit: 0.99608
********************************************************************************
Point System Name: BI2SS
Point Name: BI2SS
Point Type: L2SL
Descriptor: A2 STRT STOP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 06 04
Inverted: No
Proof Point Address: 0 01 01
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: BI2SSP
Point Name: BI2SSP
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BI2SSR
Point Name: BI2SSR
Point Type: LDO
Descriptor: A2 EMG RUN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 06 03
Inverted: No
********************************************************************************
Point System Name: BI2SSS
Point Name: BI2SSS
Point Type: LDO
Descriptor: A2 EMG STOP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 06 01
Inverted: No
********************************************************************************
Point System Name: BI2VFL
Point Name: BI2VFL
Point Type: LDI
Descriptor: A2 VFD FLT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 2 25 93
Normally Closed: No
********************************************************************************
Point System Name: BI2VRL
Point Name: BI2VRL
Point Type: LDO
Descriptor: VFD ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BI2VRL.IN.OPERATOR
Point Name: BI2VRL.IN.OPERATOR
Point Type: LDO
Descriptor: VFD ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BI2XCN
Point Name: BI2XCN
Point Type: LDO
Descriptor: A2 A1 XCON
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 08 02
Inverted: No
********************************************************************************
Point System Name: BI2Z1T
Point Name: BI2Z1T
Point Type: LAI
Descriptor: B14 TEMP
Value: 76.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2Z2T
Point Name: BI2Z2T
Point Type: LAI
Descriptor: 115 TEMP
Value: 75.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2Z3T
Point Name: BI2Z3T
Point Type: LAI
Descriptor: 118 TEMP
Value: 72.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2Z4T
Point Name: BI2Z4T
Point Type: LAI
Descriptor: 213 TEMP
Value: 74.78
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2Z5T
Point Name: BI2Z5T
Point Type: LAI
Descriptor: 218 TEMP
Value: 69.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2Z6T
Point Name: BI2Z6T
Point Type: LAI
Descriptor: 220A TEMP
Value: 72.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2Z7T
Point Name: BI2Z7T
Point Type: LAI
Descriptor: 327 TEMP
Value: 78.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 09 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2Z8T
Point Name: BI2Z8T
Point Type: LAI
Descriptor: 334 TEMP
Value: 76.87
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 10 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI2ZAH
Point Name: BI2ZAH
Point Type: LAI
Descriptor: RM328 HUMID
Value: 45.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 03 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -5.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BI300M
Point Name: BI300M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 650.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI301M
Point Name: BI301M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 650.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI302M
Point Name: BI302M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI307M
Point Name: BI307M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI310M
Point Name: BI310M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1500.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI315M
Point Name: BI315M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI319M
Point Name: BI319M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI320M
Point Name: BI320M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI326M
Point Name: BI326M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1360.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI327M
Point Name: BI327M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1420.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI329M
Point Name: BI329M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 800.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI334M
Point Name: BI334M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 1500.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI3BRL
Point Name: BI3BRL
Point Type: LDO
Descriptor: BYPAS ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BI3BYP
Point Name: BI3BYP
Point Type: LDI
Descriptor: BYP STATUS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 10 04
Normally Closed: No
********************************************************************************
Point System Name: BI3CCT
Point Name: BI3CCT
Point Type: LAI
Descriptor: A3 CCL TEMP
Value: 53.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3CCV
Point Name: BI3CCV
Point Type: LAO
Descriptor: A3 CCOIL VLV
Value: 8.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 04 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI3CFM
Point Name: BI3CFM
Point Type: LAO
Descriptor: AH3 AIR VOLU
Value: 15047.44
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 500.0
********************************************************************************
Point System Name: BI3DSC
Point Name: BI3DSC
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BI3DSP
Point Name: BI3DSP
Point Type: LAI
Descriptor: A3 SA STATIC
Value: 1.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BI3FFP
Point Name: BI3FFP
Point Type: LDI
Descriptor: A3 FNL FLTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 01 03
Normally Closed: No
********************************************************************************
Point System Name: BI3FRZ
Point Name: BI3FRZ
Point Type: LDI
Descriptor: A3 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 01 04
Normally Closed: No
********************************************************************************
Point System Name: BI3FSP
Point Name: BI3FSP
Point Type: LAO
Descriptor: A3 SPD CTRL
Value: 6.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 03 06
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BI3HMC
Point Name: BI3HMC
Point Type: LAO
Descriptor: ZONE HUM SET
Value: 30.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI3HME
Point Name: BI3HME
Point Type: LDO
Descriptor: A3 HUM ENA
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 06 06
Inverted: No
********************************************************************************
Point System Name: BI3HMV
Point Name: BI3HMV
Point Type: LAO
Descriptor: A3 HUM VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 04 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI3HRC
Point Name: BI3HRC
Point Type: LAO
Descriptor: HR SUP TEMP
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI3HRT
Point Name: BI3HRT
Point Type: LAI
Descriptor: A3HTREC TMP
Value: 66.9
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3HRV
Point Name: BI3HRV
Point Type: LAO
Descriptor: A3 HREC VLV
Value: 3.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 04 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI3HSP
Point Name: BI3HSP
Point Type: LDO
Descriptor: HIGH STATIC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BI3HT1
Point Name: BI3HT1
Point Type: LAI
Descriptor: A3 HC1 TEMP
Value: 67.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 10 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 2.54
COV Limit: 0.996
********************************************************************************
Point System Name: BI3HT2
Point Name: BI3HT2
Point Type: LAI
Descriptor: A3 HC2 TEMP
Value: 65.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 10 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.54
COV Limit: 0.996
********************************************************************************
Point System Name: BI3HV1
Point Name: BI3HV1
Point Type: LAO
Descriptor: A3 HT VLV1
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 04 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI3HV2
Point Name: BI3HV2
Point Type: LAO
Descriptor: A3 HT VLV2
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 04 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI3OCC
Point Name: BI3OCC
Point Type: LDO
Descriptor: OCCUPIED ENA
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BI3PFP
Point Name: BI3PFP
Point Type: LDI
Descriptor: A3 PREIFLTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 01 02
Normally Closed: No
********************************************************************************
Point System Name: BI3PHT
Point Name: BI3PHT
Point Type: LAI
Descriptor: A3 PHT TEMP
Value: 66.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 10 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.54
COV Limit: 0.996
********************************************************************************
Point System Name: BI3PHV
Point Name: BI3PHV
Point Type: LAO
Descriptor: A3 PHT VLV
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 04 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BI3RRC
Point Name: BI3RRC
Point Type: LAO
Descriptor: HT REC RET T
Value: 32.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI3RRT
Point Name: BI3RRT
Point Type: LAI
Descriptor: A3 HREC RTMP
Value: 73.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3SAC
Point Name: BI3SAC
Point Type: LAO
Descriptor: SUP AIR SET
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BI3SAT
Point Name: BI3SAT
Point Type: LAI
Descriptor: A3 SA TEMP
Value: 55.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.87865
COV Limit: 0.996
********************************************************************************
Point System Name: BI3SAV
Point Name: BI3SAV
Point Type: LAI
Descriptor: A3 VEL PRESS
Value: 36.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: UINH2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.020345
Intercept: -124.99928
COV Limit: 0.99608
********************************************************************************
Point System Name: BI3SS
Point Name: BI3SS
Point Type: L2SL
Descriptor: A3 STRT STOP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 07 06
Inverted: No
Proof Point Address: 0 01 01
Normally Closed: No
Proof Delay: 40 Informational Text
********************************************************************************
Point System Name: BI3SSP
Point Name: BI3SSP
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BI3SSR
Point Name: BI3SSR
Point Type: LDO
Descriptor: A3 EMG RUN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 06 05
Inverted: No
********************************************************************************
Point System Name: BI3SSS
Point Name: BI3SSS
Point Type: LDO
Descriptor: A3 EMG STOP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 07 01
Inverted: No
********************************************************************************
Point System Name: BI3VFL
Point Name: BI3VFL
Point Type: LDI
Descriptor: A3 VFD FLT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 01 05
Normally Closed: No
********************************************************************************
Point System Name: BI3VFP
Point Name: BI3VFP
Point Type: LAI
Descriptor: A3 VFD SPD
Value: 61.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 1.99987
********************************************************************************
Point System Name: BI3VRL
Point Name: BI3VRL
Point Type: LDO
Descriptor: VFD ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BI3VRL.IN.OPERATOR
Point Name: BI3VRL.IN.OPERATOR
Point Type: LDO
Descriptor: VFD ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BI3XCN
Point Name: BI3XCN
Point Type: LDO
Descriptor: A2 A3 XCON
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 08 03
Inverted: No
********************************************************************************
Point System Name: BI3Z2T
Point Name: BI3Z2T
Point Type: LAI
Descriptor: 102 TEMP
Value: 75.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 55.0
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3Z3T
Point Name: BI3Z3T
Point Type: LAI
Descriptor: 103 TEMP
Value: 76.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3Z4T
Point Name: BI3Z4T
Point Type: LAI
Descriptor: 202 TEMP
Value: 73.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3Z5T
Point Name: BI3Z5T
Point Type: LAI
Descriptor: 203 TEMP
Value: 70.93
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3Z6T
Point Name: BI3Z6T
Point Type: LAI
Descriptor: 302 TEMP
Value: 74.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BI3Z7T
Point Name: BI3Z7T
Point Type: LAI
Descriptor: 303A RM TEMP
Value: 72.66
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.98
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 09 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.46
COV Limit: 0.996
********************************************************************************
Point System Name: BI3ZAH
Point Name: BI3ZAH
Point Type: LAI
Descriptor: 303A HUMID
Value: 32.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -14.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BI95DT
Point Name: BI95DT
Point Type: LAO
Descriptor: DAY TMP SP
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIA1S
Point Name: BIA1S
Point Type: L2SL
Descriptor: AH1 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
On/Off Point Address: 3 01 24
Inverted: No
Proof Point Address: 3 01 23
Normally Closed: No
Proof Delay: 120 Informational Text
********************************************************************************
Point System Name: BIA1VS
Point Name: BIA1VS
Point Type: LAO
Descriptor: AH1 VFD SPEED
Value: 90.9671
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 4
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 3 01 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIA2S
Point Name: BIA2S
Point Type: L2SL
Descriptor: AH1 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 2 25 24
Inverted: No
Proof Point Address: 2 25 23
Normally Closed: No
Proof Delay: 120 Informational Text
********************************************************************************
Point System Name: BIA2VFDOK.FAULT
Point Name: BIA2VFDOK.FAULT
Point Type: LDI
Descriptor: VFD
Value: OK
Condition: -N-
Priority: NONE
Text Table: OK_FAULT
0 - OK
1 - FAULT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 2 25 93
Normally Closed: No
********************************************************************************
Point System Name: BIA2VFDRESET FAULT
Point Name: BIA2VFDRESET FAULT
Point Type: LDO
Descriptor: VFD
Value: NO
Condition: -N-
Priority: NONE
Text Table: NO_RESET
0 - NO
1 - RESET
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 2 25 94
Inverted: No
********************************************************************************
Point System Name: BIB02ARM
Point Name: BIB02ARM
Point Type: LAI
Descriptor: ROOM B02A TEMP
Value: 0.0
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 2 20 14
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.1
Intercept: -42.0
COV Limit: 0.5
********************************************************************************
Point System Name: BIB02M
Point Name: BIB02M
Point Type: LAO
Descriptor: MAX SUP AIR STPT
Value: 680.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: CFM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIC1V1
Point Name: BIC1V1
Point Type: LAO
Descriptor: CONV1 VLV1
Value: 4.95
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 09 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIC1V2
Point Name: BIC1V2
Point Type: LAO
Descriptor: CONV1 VLV2
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 09 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIC2V1
Point Name: BIC2V1
Point Type: LAO
Descriptor: CONV2 VLV1
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 09 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIC2V2
Point Name: BIC2V2
Point Type: LAO
Descriptor: CONV2 VLV2
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 09 08
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BICHRT
Point Name: BICHRT
Point Type: LAI
Descriptor: CHWR TEMP
Value: 55.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BICHST
Point Name: BICHST
Point Type: LAI
Descriptor: CHWS TEMP
Value: 47.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BICONM
Point Name: BICONM
Point Type: LPACI
Descriptor: CON METER
Value: 655660.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 12 02
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
********************************************************************************
Point System Name: BICTLA
Point Name: BICTLA
Point Type: LDI
Descriptor: CONTROL AIR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 16
Normally Closed: No
********************************************************************************
Point System Name: BIDILD
Point Name: BIDILD
Point Type: LAO
Descriptor: DIPMP LEDLAG
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIDIP1
Point Name: BIDIP1
Point Type: L2SL
Descriptor: DI WTR PMP1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 07 04
Inverted: No
Proof Point Address: 0 02 01
Normally Closed: No
Proof Delay: 20 Informational Text
********************************************************************************
Point System Name: BIDIP2
Point Name: BIDIP2
Point Type: L2SL
Descriptor: DI WTR PMP2
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 07 05
Inverted: No
Proof Point Address: 0 02 02
Normally Closed: No
Proof Delay: 20 Informational Text
********************************************************************************
Point System Name: BIDIPD
Point Name: BIDIPD
Point Type: LAO
Descriptor: DI PMP DELAY
Value: 30.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIDIS1
Point Name: BIDIS1
Point Type: LDO
Descriptor: DI VIR TOGGL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIDIWA
Point Name: BIDIWA
Point Type: LDI
Descriptor: DIWTRALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 05
Normally Closed: No
********************************************************************************
Point System Name: BIDP1A
Point Name: BIDP1A
Point Type: LDO
Descriptor: DI PMP ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIDP2A
Point Name: BIDP2A
Point Type: LDO
Descriptor: DI PMP ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE01A
Point Name: BIE01A
Point Type: LDO
Descriptor: E01 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE01C
Point Name: BIE01C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE01D
Point Name: BIE01D
Point Type: L2SL
Descriptor: E01 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 06 03
Inverted: No
Proof Point Address: 0 01 07
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE01E
Point Name: BIE01E
Point Type: LDO
Descriptor: E01 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE01P
Point Name: BIE01P
Point Type: LAI
Descriptor: E01STATIC
Value: 1.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE01R
Point Name: BIE01R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE01S
Point Name: BIE01S
Point Type: L2SL
Descriptor: E01 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 06 04
Inverted: No
Proof Point Address: 0 01 06
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE01SS
Point Name: BIE01SS
Point Type: L2SL
Descriptor: EF01 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 2 14 24
Inverted: No
Proof Point Address: 2 14 23
Normally Closed: No
Proof Delay: 10 Informational Text
********************************************************************************
Point System Name: BIE01V
Point Name: BIE01V
Point Type: LAO
Descriptor: E01 SPD CTRL
Value: 87.3
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 2 14 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIE02A
Point Name: BIE02A
Point Type: LDO
Descriptor: E02 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE02C
Point Name: BIE02C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE02D
Point Name: BIE02D
Point Type: L2SL
Descriptor: E02 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 06 06
Inverted: No
Proof Point Address: 0 01 07
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE02E
Point Name: BIE02E
Point Type: LDO
Descriptor: E02 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE02P
Point Name: BIE02P
Point Type: LAI
Descriptor: E02 STATIC
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 03 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE02R
Point Name: BIE02R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE02S
Point Name: BIE02S
Point Type: L2SL
Descriptor: E02 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 06 05
Inverted: No
Proof Point Address: 0 01 06
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE02SS
Point Name: BIE02SS
Point Type: L2SL
Descriptor: EF02 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 3 30 24
Inverted: No
Proof Point Address: 3 30 23
Normally Closed: No
Proof Delay: 120 Informational Text
********************************************************************************
Point System Name: BIE03A
Point Name: BIE03A
Point Type: LDO
Descriptor: E03 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE03C
Point Name: BIE03C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE03D
Point Name: BIE03D
Point Type: L2SL
Descriptor: E03 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 06 01
Inverted: No
Proof Point Address: 0 01 09
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE03E
Point Name: BIE03E
Point Type: LDO
Descriptor: E03 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE03P
Point Name: BIE03P
Point Type: LAI
Descriptor: E03 STATIC
Value: 1.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 02 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE03R
Point Name: BIE03R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE03S
Point Name: BIE03S
Point Type: L2SL
Descriptor: E03 STRT STP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM29
On/Off Point Address: 2 15 24
Inverted: No
Proof Point Address: 2 15 23
Normally Closed: No
Proof Delay: 10 Informational Text
********************************************************************************
Point System Name: BIE03SS
Point Name: BIE03SS
Point Type: LDO
Descriptor: EF03 START STOP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 06 02
Inverted: No
********************************************************************************
Point System Name: BIE03V
Point Name: BIE03V
Point Type: LAO
Descriptor: E03 SPD CTRL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 03 07
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BIE03VS
Point Name: BIE03VS
Point Type: LAO
Descriptor: EXF03 VFD SPEED
Value: 55.3205
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 4
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 2 15 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIE04S
Point Name: BIE04S
Point Type: L2SL
Descriptor: E04 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 05 05
Inverted: No
Proof Point Address: 0 01 11
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: BIE05S
Point Name: BIE05S
Point Type: L2SL
Descriptor: E05 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 05 06
Inverted: No
Proof Point Address: 0 01 15
Normally Closed: No
Proof Delay: 10 Informational Text
********************************************************************************
Point System Name: BIE17C
Point Name: BIE17C
Point Type: LDI
Descriptor: E17 DPR CLOS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 10
Normally Closed: No
********************************************************************************
Point System Name: BIE17O
Point Name: BIE17O
Point Type: LDI
Descriptor: E17 DPR OPEN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 09
Normally Closed: No
********************************************************************************
Point System Name: BIE17S
Point Name: BIE17S
Point Type: L2SL
Descriptor: E17 STRT STP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 06 01
Inverted: No
Proof Point Address: 0 01 08
Normally Closed: No
Proof Delay: 0 Informational Text
********************************************************************************
Point System Name: BIE18C
Point Name: BIE18C
Point Type: LDI
Descriptor: E18 DPR CLOS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 14
Normally Closed: No
********************************************************************************
Point System Name: BIE18O
Point Name: BIE18O
Point Type: LDI
Descriptor: E18 DPR OPEN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 01 13
Normally Closed: No
********************************************************************************
Point System Name: BIE18S
Point Name: BIE18S
Point Type: L2SL
Descriptor: E18 STRT STP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 06 02
Inverted: No
Proof Point Address: 0 01 12
Normally Closed: No
Proof Delay: 0 Informational Text
********************************************************************************
Point System Name: BIE19A
Point Name: BIE19A
Point Type: LDO
Descriptor: E19 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE19C
Point Name: BIE19C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.25
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE19D
Point Name: BIE19D
Point Type: L2SL
Descriptor: E19 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 07 03
Inverted: No
Proof Point Address: 0 01 11
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE19E
Point Name: BIE19E
Point Type: LDO
Descriptor: E19 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE19P
Point Name: BIE19P
Point Type: LAI
Descriptor: E19 STATIC
Value: 1.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 03 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE19R
Point Name: BIE19R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE19S
Point Name: BIE19S
Point Type: L2SL
Descriptor: E19 STRT STP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM29
On/Off Point Address: 2 13 24
Inverted: No
Proof Point Address: 2 13 23
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE19SS
Point Name: BIE19SS
Point Type: LDO
Descriptor: EF19 START STOP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 07 02
Inverted: No
********************************************************************************
Point System Name: BIE19V
Point Name: BIE19V
Point Type: LAO
Descriptor: E19 SPD CTRL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 03 05
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BIE19VS
Point Name: BIE19VS
Point Type: LAO
Descriptor: EXF19 VFD SPEED
Value: 67.6067
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 4
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 2 13 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIE20A
Point Name: BIE20A
Point Type: LDO
Descriptor: E20 ALARM
Value: OFF
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE20C
Point Name: BIE20C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE20D
Point Name: BIE20D
Point Type: L2SL
Descriptor: E20 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 07 05
Inverted: No
Proof Point Address: 0 01 13
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE20E
Point Name: BIE20E
Point Type: LDO
Descriptor: E20 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE20P
Point Name: BIE20P
Point Type: LAI
Descriptor: E20 STATIC
Value: 1.19
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 03 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE20R
Point Name: BIE20R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE20S
Point Name: BIE20S
Point Type: L2SL
Descriptor: E20 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 07 04
Inverted: No
Proof Point Address: 0 01 12
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: BIE20SS
Point Name: BIE20SS
Point Type: L2SL
Descriptor: EF02 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 2 12 24
Inverted: No
Proof Point Address: 2 12 23
Normally Closed: No
Proof Delay: 10 Informational Text
********************************************************************************
Point System Name: BIE20VS
Point Name: BIE20VS
Point Type: LAO
Descriptor: EXF20VFD SPEED
Value: 59.5499
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 4
Engineering Units: PERCNT
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 2 12 60
Actuator Type Voltage
Slope: 0.1
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIE21A
Point Name: BIE21A
Point Type: LDO
Descriptor: E21 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE21C
Point Name: BIE21C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE21D
Point Name: BIE21D
Point Type: L2SL
Descriptor: E21 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 08 02
Inverted: No
Proof Point Address: 0 01 15
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE21E
Point Name: BIE21E
Point Type: LDO
Descriptor: E21 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE21P
Point Name: BIE21P
Point Type: LAI
Descriptor: E21 STATIC
Value: 1.17
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 03 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE21R
Point Name: BIE21R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE21S
Point Name: BIE21S
Point Type: L2SL
Descriptor: E21 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 08 01
Inverted: No
Proof Point Address: 0 01 14
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE21SS
Point Name: BIE21SS
Point Type: L2SL
Descriptor: EF21 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
On/Off Point Address: 2 16 24
Inverted: No
Proof Point Address: 2 16 23
Normally Closed: No
Proof Delay: 10 Informational Text
********************************************************************************
Point System Name: BIE21V
Point Name: BIE21V
Point Type: LAO
Descriptor: EX 21 SPD CTL
Value: 76.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PRCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIE22A
Point Name: BIE22A
Point Type: LDO
Descriptor: E22 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE22C
Point Name: BIE22C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE22D
Point Name: BIE22D
Point Type: L2SL
Descriptor: E22 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 07 02
Inverted: No
Proof Point Address: 0 01 09
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE22E
Point Name: BIE22E
Point Type: LDO
Descriptor: E22 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE22P
Point Name: BIE22P
Point Type: LAI
Descriptor: E22 STATIC
Value: 1.22
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 03 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE22R
Point Name: BIE22R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE22S
Point Name: BIE22S
Point Type: L2SL
Descriptor: E22 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 07 01
Inverted: No
Proof Point Address: 0 01 08
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE22V
Point Name: BIE22V
Point Type: LAO
Descriptor: E22 SPD CTRL
Value: 5.84
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 05
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BIE23A
Point Name: BIE23A
Point Type: LDO
Descriptor: E23 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE23C
Point Name: BIE23C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE23D
Point Name: BIE23D
Point Type: L2SL
Descriptor: E23 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 07 04
Inverted: No
Proof Point Address: 0 01 11
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE23E
Point Name: BIE23E
Point Type: LDO
Descriptor: E23 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE23P
Point Name: BIE23P
Point Type: LAI
Descriptor: E23 STATIC
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 03 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.1
********************************************************************************
Point System Name: BIE23R
Point Name: BIE23R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE23S
Point Name: BIE23S
Point Type: L2SL
Descriptor: E23 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 07 03
Inverted: No
Proof Point Address: 0 01 10
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE23SS
Point Name: BIE23SS
Point Type: L2SL
Descriptor: EF23 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 3 31 24
Inverted: No
Proof Point Address: 3 31 23
Normally Closed: No
Proof Delay: 15 Informational Text
********************************************************************************
Point System Name: BIE23V
Point Name: BIE23V
Point Type: LAO
Descriptor: E23 SPD CTRL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 03 07
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE24A
Point Name: BIE24A
Point Type: LDO
Descriptor: E24 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE24C
Point Name: BIE24C
Point Type: LAO
Descriptor: STATIC SET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE24D
Point Name: BIE24D
Point Type: L2SL
Descriptor: E24 ISOL DMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 07 06
Inverted: No
Proof Point Address: 0 01 13
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE24E
Point Name: BIE24E
Point Type: LDO
Descriptor: E24 ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE24P
Point Name: BIE24P
Point Type: LAI
Descriptor: E24 STATIC
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.1
********************************************************************************
Point System Name: BIE24R
Point Name: BIE24R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 1.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE24S
Point Name: BIE24S
Point Type: L2SL
Descriptor: E24 STRT STP
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 07 05
Inverted: No
Proof Point Address: 0 01 12
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIE24SS
Point Name: BIE24SS
Point Type: L2SL
Descriptor: EF24 START STOP
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
On/Off Point Address: 3 29 24
Inverted: No
Proof Point Address: 3 29 23
Normally Closed: No
Proof Delay: 120 Informational Text
********************************************************************************
Point System Name: BIE25A
Point Name: BIE25A
Point Type: LDO
Descriptor: E25 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE25C
Point Name: BIE25C
Point Type: LAO
Descriptor: STATIC SET
Value: 2.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE25E
Point Name: BIE25E
Point Type: LDO
Descriptor: E25 ENABLE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE25P
Point Name: BIE25P
Point Type: LAI
Descriptor: E25 STATIC
Value: 1.59
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 03 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE25R
Point Name: BIE25R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 2.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE25S
Point Name: BIE25S
Point Type: L2SL
Descriptor: E25 STRT STP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM29
On/Off Point Address: 0 08 04
Inverted: No
Proof Point Address: 0 01 16
Normally Closed: No
Proof Delay: 120 Informational Text
********************************************************************************
Point System Name: BIE25V
Point Name: BIE25V
Point Type: LAO
Descriptor: E25 SPD CTRL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: 0 04 08
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BIE26A
Point Name: BIE26A
Point Type: LDO
Descriptor: E26 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE26C
Point Name: BIE26C
Point Type: LAO
Descriptor: STATIC SET
Value: 2.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE26E
Point Name: BIE26E
Point Type: LDO
Descriptor: E26 ENABLE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIE26P
Point Name: BIE26P
Point Type: LAI
Descriptor: E26 STATIC
Value: 1.29
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24909
COV Limit: 0.10003
********************************************************************************
Point System Name: BIE26R
Point Name: BIE26R
Point Type: LAO
Descriptor: STAT LOOPSET
Value: 2.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.1
********************************************************************************
Point System Name: BIE26S
Point Name: BIE26S
Point Type: L2SL
Descriptor: E26 STRT STP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM28
On/Off Point Address: 0 08 01
Inverted: No
Proof Point Address: 0 01 14
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: BIE26V
Point Name: BIE26V
Point Type: LAO
Descriptor: E26 SPD CTRL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 04 08
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BIELVR
Point Name: BIELVR
Point Type: L2SL
Descriptor: ELEV DMPR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 06 05
Inverted: No
Proof Point Address: 0 01 16
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: BIEMTS
Point Name: BIEMTS
Point Type: LDI
Descriptor: EM TRANS SW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 04
Normally Closed: No
********************************************************************************
Point System Name: BIG1.CLOSE.SHADE.HEAT
Point Name: BIG1.CLOSE.SHADE.HEAT
Point Type: LDO
Descriptor: HEAT CONSERV
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.CLOSE.SHADE.LITE
Point Name: BIG1.CLOSE.SHADE.LITE
Point Type: LDO
Descriptor: DRAPE CLOSE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.CLOSE.SHADES
Point Name: BIG1.CLOSE.SHADES
Point Type: LDO
Descriptor: SHADE SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.CO2
Point Name: BIG1.CO2
Point Type: LAI
Descriptor: R121E CO2
Value: -500.0
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.08138
Intercept: -499.99997
COV Limit: 10.0
********************************************************************************
Point System Name: BIG1.CO2.BR
Point Name: BIG1.CO2.BR
Point Type: LDO
Descriptor: R121E CO2 BR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 07 04
Inverted: No
********************************************************************************
Point System Name: BIG1.DAY.LITE.LVL
Point Name: BIG1.DAY.LITE.LVL
Point Type: LAO
Descriptor: DAY EXT LVL
Value: 2000.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.DAY.MODE
Point Name: BIG1.DAY.MODE
Point Type: LDO
Descriptor: DAY MODE SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.DAY.RMS
Point Name: BIG1.DAY.RMS
Point Type: LAO
Descriptor: DAY TEMP SET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.EF.FAST.ENA
Point Name: BIG1.EF.FAST.ENA
Point Type: LDO
Descriptor: EXH FAN FAST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.EF.FAST.SS
Point Name: BIG1.EF.FAST.SS
Point Type: LDO
Descriptor: EXH FAN FAST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 06 01
Inverted: No
********************************************************************************
Point System Name: BIG1.EF.SLOW.ENA
Point Name: BIG1.EF.SLOW.ENA
Point Type: LDO
Descriptor: EXH FAN SLOW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.EF.SLOW.SS
Point Name: BIG1.EF.SLOW.SS
Point Type: LDO
Descriptor: EXH FAN SLOW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 06 02
Inverted: No
********************************************************************************
Point System Name: BIG1.FAN.LOCKOUT
Point Name: BIG1.FAN.LOCKOUT
Point Type: LDO
Descriptor: FAN LOCKOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.HID.LITES
Point Name: BIG1.HID.LITES
Point Type: LDO
Descriptor: HID LITES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 04 02
Inverted: No
********************************************************************************
Point System Name: BIG1.HIGH.INT.LITE.DELAY
Point Name: BIG1.HIGH.INT.LITE.DELAY
Point Type: LAO
Descriptor: TIME DELAY
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MINUTE
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.INC.LITES
Point Name: BIG1.INC.LITES
Point Type: LDO
Descriptor: INCAN LITES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 04 01
Inverted: No
********************************************************************************
Point System Name: BIG1.LITE.HID.ENA
Point Name: BIG1.LITE.HID.ENA
Point Type: LDO
Descriptor: HID DBSWIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.LITE.INC.ENA
Point Name: BIG1.LITE.INC.ENA
Point Type: LDO
Descriptor: INC DBSWIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.LITE.INTENSITY
Point Name: BIG1.LITE.INTENSITY
Point Type: LAO
Descriptor: LITE INTSTY
Value: 3876.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 30.21333
********************************************************************************
Point System Name: BIG1.LOOP.MAX
Point Name: BIG1.LOOP.MAX
Point Type: LAO
Descriptor: LOOP MAX OUT
Value: 99.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.LOOPOUT
Point Name: BIG1.LOOPOUT
Point Type: LAO
Descriptor: TEMP LOOPOUT
Value: 62.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.MAN.VENT.LOCK
Point Name: BIG1.MAN.VENT.LOCK
Point Type: LDO
Descriptor: VENT LOCKOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.N.VENT.CLOSE
Point Name: BIG1.N.VENT.CLOSE
Point Type: LDO
Descriptor: NO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.NITE.RMS
Point Name: BIG1.NITE.RMS
Point Type: LAO
Descriptor: NGT TEMP SET
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.PUMP.LOCKOUT
Point Name: BIG1.PUMP.LOCKOUT
Point Type: LAO
Descriptor: PUMP LOCKOUT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.PUMP.SS
Point Name: BIG1.PUMP.SS
Point Type: LDO
Descriptor: R121E PUMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 07 02
Inverted: No
********************************************************************************
Point System Name: BIG1.RAD.HIGH
Point Name: BIG1.RAD.HIGH
Point Type: LAO
Descriptor: R121E RAD HI
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIG1.RAD.LOW
Point Name: BIG1.RAD.LOW
Point Type: LAO
Descriptor: R121E RAD LO
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIG1.RMH
Point Name: BIG1.RMH
Point Type: LAI
Descriptor: R121E HUMID
Value: 1.73
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 01 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.99829
COV Limit: 3.0
********************************************************************************
Point System Name: BIG1.RMS
Point Name: BIG1.RMS
Point Type: LAI
Descriptor: ROOM TEMPSET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.RMT
Point Name: BIG1.RMT
Point Type: LAI
Descriptor: R121E ZN TMP
Value: 73.68
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Enhanced Alarms
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 01 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.46
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1.S.VENT.CLOSE
Point Name: BIG1.S.VENT.CLOSE
Point Type: LDO
Descriptor: SO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.VENT.RESET
Point Name: BIG1.VENT.RESET
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 1 01 94
Normally Closed: No
********************************************************************************
Point System Name: BIG1.VENT.SKIP
Point Name: BIG1.VENT.SKIP
Point Type: LDO
Descriptor: VENT SKIP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1.WATTS.METER
Point Name: BIG1.WATTS.METER
Point Type: LAI
Descriptor: WATTSQMTR
Value: 62.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: WSQMTR
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.055896
Intercept: -343.42453
COV Limit: 1.01954
********************************************************************************
Point System Name: BIG101
Point Name: BIG101
Point Type: LDO
Descriptor: RESET TOGGLE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG102
Point Name: BIG102
Point Type: LDO
Descriptor: SV OPEN QTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG103
Point Name: BIG103
Point Type: LDO
Descriptor: SV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG104
Point Name: BIG104
Point Type: LDO
Descriptor: SV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG105
Point Name: BIG105
Point Type: LDO
Descriptor: SV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG106
Point Name: BIG106
Point Type: LDO
Descriptor: SV CLOSE QTR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG107
Point Name: BIG107
Point Type: LDO
Descriptor: SV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG108
Point Name: BIG108
Point Type: LDO
Descriptor: NV OPEN QTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG109
Point Name: BIG109
Point Type: LDO
Descriptor: NV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG110
Point Name: BIG110
Point Type: LDO
Descriptor: NV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG111
Point Name: BIG111
Point Type: LDO
Descriptor: NV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG112
Point Name: BIG112
Point Type: LDO
Descriptor: NV CLOSE QTR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG113
Point Name: BIG113
Point Type: LDO
Descriptor: NV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG114
Point Name: BIG114
Point Type: LDO
Descriptor: LV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG115
Point Name: BIG115
Point Type: LDO
Descriptor: LV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG116
Point Name: BIG116
Point Type: LDO
Descriptor: LV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG117
Point Name: BIG117
Point Type: LDO
Descriptor: LV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG118
Point Name: BIG118
Point Type: LAO
Descriptor: 1 SOLAR SHADE LO
Value: 25000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
********************************************************************************
Point System Name: BIG120
Point Name: BIG120
Point Type: LDO
Descriptor: OPEN SLOW SW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1CL
Point Name: BIG1CL
Point Type: LDO
Descriptor: LO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1DC
Point Name: BIG1DC
Point Type: LDO
Descriptor: R121E SHD CL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 05 02
Inverted: No
********************************************************************************
Point System Name: BIG1DO
Point Name: BIG1DO
Point Type: LDO
Descriptor: R121E SHD OP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 05 01
Inverted: No
********************************************************************************
Point System Name: BIG1HOLD1
Point Name: BIG1HOLD1
Point Type: LAO
Descriptor: HOLDER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MINUTE
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1HS
Point Name: BIG1HS
Point Type: LAO
Descriptor: H RAD SET ON
Value: 32.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1LC
Point Name: BIG1LC
Point Type: LDO
Descriptor: R121E S VENT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 08 04
Inverted: No
********************************************************************************
Point System Name: BIG1LH
Point Name: BIG1LH
Point Type: LDO
Descriptor: HID TOD SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1LL
Point Name: BIG1LL
Point Type: LDO
Descriptor: INC TOD SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1LO
Point Name: BIG1LO
Point Type: LDO
Descriptor: R121E S VENT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 08 03
Inverted: No
********************************************************************************
Point System Name: BIG1LV
Point Name: BIG1LV
Point Type: LAO
Descriptor: LO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG1NC
Point Name: BIG1NC
Point Type: LDO
Descriptor: R121E N RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 08 01
Inverted: No
********************************************************************************
Point System Name: BIG1NO
Point Name: BIG1NO
Point Type: LDO
Descriptor: R121E N RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 08 02
Inverted: No
********************************************************************************
Point System Name: BIG1NV
Point Name: BIG1NV
Point Type: LAO
Descriptor: NO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG1PS
Point Name: BIG1PS
Point Type: LAO
Descriptor: PHOTO SYN LV
Value: 20000.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1RV
Point Name: BIG1RV
Point Type: LAO
Descriptor: VENT SETTING
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG1S1
Point Name: BIG1S1
Point Type: LAO
Descriptor: SECNDS
Value: 1165.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S2
Point Name: BIG1S2
Point Type: LAO
Descriptor: SECNDS
Value: 305.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S3
Point Name: BIG1S3
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S4
Point Name: BIG1S4
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S5
Point Name: BIG1S5
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S6
Point Name: BIG1S6
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S7
Point Name: BIG1S7
Point Type: LAO
Descriptor: SECNDS
Value: 180.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S8
Point Name: BIG1S8
Point Type: LAO
Descriptor: SECNDS
Value: 2000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1S9
Point Name: BIG1S9
Point Type: LAO
Descriptor: SECNDS
Value: 1800.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1SC
Point Name: BIG1SC
Point Type: LDO
Descriptor: R121E S RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 08 06
Inverted: No
********************************************************************************
Point System Name: BIG1SI
Point Name: BIG1SI
Point Type: LAO
Descriptor: 1 SOLAR SHADE HI
Value: 30000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
********************************************************************************
Point System Name: BIG1SO
Point Name: BIG1SO
Point Type: LDO
Descriptor: R121E S RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 08 05
Inverted: No
********************************************************************************
Point System Name: BIG1SV
Point Name: BIG1SV
Point Type: LAO
Descriptor: SO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG1V1
Point Name: BIG1V1
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1V2
Point Name: BIG1V2
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1V3
Point Name: BIG1V3
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1V4
Point Name: BIG1V4
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1V5
Point Name: BIG1V5
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1V6
Point Name: BIG1V6
Point Type: LDO
Descriptor: VNT CNT SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG1X1
Point Name: BIG1X1
Point Type: LAO
Descriptor: TEST LOC1
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1X2
Point Name: BIG1X2
Point Type: LAO
Descriptor: TEST LOC2
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG1X3
Point Name: BIG1X3
Point Type: LAO
Descriptor: TEST LOC3
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.CLOSE.SHADE.HEAT
Point Name: BIG2.CLOSE.SHADE.HEAT
Point Type: LDO
Descriptor: HEAT CONSERV
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.CLOSE.SHADE.LITE
Point Name: BIG2.CLOSE.SHADE.LITE
Point Type: LDO
Descriptor: DRAPE CLOSE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.CLOSE.SHADES
Point Name: BIG2.CLOSE.SHADES
Point Type: LDO
Descriptor: SHADE SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.CO2
Point Name: BIG2.CO2
Point Type: LAI
Descriptor: R121F CO2
Value: -500.0
Condition: *OF*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.08138
Intercept: -499.99997
COV Limit: 10.0
********************************************************************************
Point System Name: BIG2.CO2.BR
Point Name: BIG2.CO2.BR
Point Type: LDO
Descriptor: R121F CO2 BR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 07 05
Inverted: No
********************************************************************************
Point System Name: BIG2.DAY.LITE.LVL
Point Name: BIG2.DAY.LITE.LVL
Point Type: LAO
Descriptor: DAY EXT LVL
Value: 2000.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.DAY.MODE
Point Name: BIG2.DAY.MODE
Point Type: LDO
Descriptor: DAY MODE SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.DAY.RMS
Point Name: BIG2.DAY.RMS
Point Type: LAO
Descriptor: DAY TEMP SET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.EF.FAST.ENA
Point Name: BIG2.EF.FAST.ENA
Point Type: LDO
Descriptor: EXH FAN FAST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.EF.FAST.SS
Point Name: BIG2.EF.FAST.SS
Point Type: LDO
Descriptor: EXH FAN FAST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 06 04
Inverted: No
********************************************************************************
Point System Name: BIG2.EF.SLOW.ENA
Point Name: BIG2.EF.SLOW.ENA
Point Type: LDO
Descriptor: EXH FAN SLOW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.EF.SLOW.SS
Point Name: BIG2.EF.SLOW.SS
Point Type: LDO
Descriptor: EXH FAN SLOW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 06 03
Inverted: No
********************************************************************************
Point System Name: BIG2.FAN.LOCKOUT
Point Name: BIG2.FAN.LOCKOUT
Point Type: LDO
Descriptor: FAN LOCKOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.HID.LITES
Point Name: BIG2.HID.LITES
Point Type: LDO
Descriptor: HID LITES
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 04 03
Inverted: No
********************************************************************************
Point System Name: BIG2.HIGH.INT.LITE.DELAY
Point Name: BIG2.HIGH.INT.LITE.DELAY
Point Type: LAO
Descriptor: TIME DELAY
Value: 1.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: MINUTE
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.INC.LITES
Point Name: BIG2.INC.LITES
Point Type: LDO
Descriptor: INCAN LITES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 04 04
Inverted: No
********************************************************************************
Point System Name: BIG2.LITE.HID.ENA
Point Name: BIG2.LITE.HID.ENA
Point Type: LDO
Descriptor: HID DBSWIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.LITE.INC.ENA
Point Name: BIG2.LITE.INC.ENA
Point Type: LDO
Descriptor: INC DBSWIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.LITE.INTENSITY
Point Name: BIG2.LITE.INTENSITY
Point Type: LAO
Descriptor: LITE INTSTY
Value: 19594.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 30.21333
********************************************************************************
Point System Name: BIG2.LOOP.MAX
Point Name: BIG2.LOOP.MAX
Point Type: LAO
Descriptor: LOOP MAX OUT
Value: 99.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.LOOPOUT
Point Name: BIG2.LOOPOUT
Point Type: LAO
Descriptor: TEMP LOOPOUT
Value: 70.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.MAN.VENT.LOCK
Point Name: BIG2.MAN.VENT.LOCK
Point Type: LDO
Descriptor: VENT LOCKOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.N.VENT.CLOSE
Point Name: BIG2.N.VENT.CLOSE
Point Type: LDO
Descriptor: NO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.NITE.RMS
Point Name: BIG2.NITE.RMS
Point Type: LAO
Descriptor: NGT TEMP SET
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.PUMP.LOCKOUT
Point Name: BIG2.PUMP.LOCKOUT
Point Type: LAO
Descriptor: PUMP LOCKOUT
Value: 50.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.PUMP.SS
Point Name: BIG2.PUMP.SS
Point Type: LDO
Descriptor: R121F PUMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 07 01
Inverted: No
********************************************************************************
Point System Name: BIG2.RAD.HIGH
Point Name: BIG2.RAD.HIGH
Point Type: LAO
Descriptor: R121F RAD HI
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIG2.RAD.LOW
Point Name: BIG2.RAD.LOW
Point Type: LAO
Descriptor: R121F RAD LOW
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIG2.RMH
Point Name: BIG2.RMH
Point Type: LAI
Descriptor: R121F HUMID
Value: 4.97
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 01 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.99911
COV Limit: 3.0
********************************************************************************
Point System Name: BIG2.RMS
Point Name: BIG2.RMS
Point Type: LAI
Descriptor: ROOM TEMPSET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.RMT
Point Name: BIG2.RMT
Point Type: LAI
Descriptor: R121F ZN TMP
Value: 74.68
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Enhanced Alarms
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 01 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.46
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2.S.VENT.CLOSE
Point Name: BIG2.S.VENT.CLOSE
Point Type: LDO
Descriptor: SO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.VENT.RESET
Point Name: BIG2.VENT.RESET
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 1 02 94
Normally Closed: No
********************************************************************************
Point System Name: BIG2.VENT.SKIP
Point Name: BIG2.VENT.SKIP
Point Type: LDO
Descriptor: VENT SKIP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2.WATTS.METER
Point Name: BIG2.WATTS.METER
Point Type: LAI
Descriptor: WATTSQMTR
Value: 315.71
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: WSQMTR
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.053625
Intercept: -329.47366
COV Limit: 1.0296
********************************************************************************
Point System Name: BIG201
Point Name: BIG201
Point Type: LDO
Descriptor: RESET TOGGLE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG202
Point Name: BIG202
Point Type: LDO
Descriptor: SV OPEN QTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG203
Point Name: BIG203
Point Type: LDO
Descriptor: SV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG204
Point Name: BIG204
Point Type: LDO
Descriptor: SV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG205
Point Name: BIG205
Point Type: LDO
Descriptor: SV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG206
Point Name: BIG206
Point Type: LDO
Descriptor: SV CLOSE QTR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG207
Point Name: BIG207
Point Type: LDO
Descriptor: SV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG208
Point Name: BIG208
Point Type: LDO
Descriptor: NV OPEN QTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG209
Point Name: BIG209
Point Type: LDO
Descriptor: NV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG210
Point Name: BIG210
Point Type: LDO
Descriptor: NV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG211
Point Name: BIG211
Point Type: LDO
Descriptor: NV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG212
Point Name: BIG212
Point Type: LDO
Descriptor: NV CLOSE QTR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG213
Point Name: BIG213
Point Type: LDO
Descriptor: NV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG214
Point Name: BIG214
Point Type: LDO
Descriptor: LV OPEN HALF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG215
Point Name: BIG215
Point Type: LDO
Descriptor: LV OPEN FULL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG216
Point Name: BIG216
Point Type: LDO
Descriptor: LV CLOSE HLF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG217
Point Name: BIG217
Point Type: LDO
Descriptor: LV CLOSE FUL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG218
Point Name: BIG218
Point Type: LAO
Descriptor: 2 SOLAR SHADE LO
Value: 25000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
********************************************************************************
Point System Name: BIG220
Point Name: BIG220
Point Type: LDO
Descriptor: OPEN SLOW SW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2CL
Point Name: BIG2CL
Point Type: LDO
Descriptor: LO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2DC
Point Name: BIG2DC
Point Type: LDO
Descriptor: R121F SHD CL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 05 04
Inverted: No
********************************************************************************
Point System Name: BIG2DO
Point Name: BIG2DO
Point Type: LDO
Descriptor: R121F SHD OP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 05 03
Inverted: No
********************************************************************************
Point System Name: BIG2HOLD1
Point Name: BIG2HOLD1
Point Type: LAO
Descriptor: HOLDER
Value: 2.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: MINUTE
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2HS
Point Name: BIG2HS
Point Type: LAO
Descriptor: H RAD SET ON
Value: 32.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2LC
Point Name: BIG2LC
Point Type: LDO
Descriptor: R121F S VENT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 09 01
Inverted: No
********************************************************************************
Point System Name: BIG2LH
Point Name: BIG2LH
Point Type: LDO
Descriptor: HID TOD SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2LL
Point Name: BIG2LL
Point Type: LDO
Descriptor: INC TOD SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2LO
Point Name: BIG2LO
Point Type: LDO
Descriptor: R121F S VENT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 09 02
Inverted: No
********************************************************************************
Point System Name: BIG2LV
Point Name: BIG2LV
Point Type: LAO
Descriptor: LO VENT SET
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG2NC
Point Name: BIG2NC
Point Type: LDO
Descriptor: R121F N RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 09 03
Inverted: No
********************************************************************************
Point System Name: BIG2NO
Point Name: BIG2NO
Point Type: LDO
Descriptor: R121F N RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 09 04
Inverted: No
********************************************************************************
Point System Name: BIG2NV
Point Name: BIG2NV
Point Type: LAO
Descriptor: NO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG2PS
Point Name: BIG2PS
Point Type: LAO
Descriptor: PHOTO SYN LV
Value: 12000.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2RV
Point Name: BIG2RV
Point Type: LAO
Descriptor: VENT SETTING
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG2S1
Point Name: BIG2S1
Point Type: LAO
Descriptor: SECNDS
Value: 1200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S2
Point Name: BIG2S2
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S3
Point Name: BIG2S3
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S4
Point Name: BIG2S4
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S5
Point Name: BIG2S5
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S6
Point Name: BIG2S6
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S7
Point Name: BIG2S7
Point Type: LAO
Descriptor: SECNDS
Value: 1200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S8
Point Name: BIG2S8
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2S9
Point Name: BIG2S9
Point Type: LAO
Descriptor: SECNDS
Value: 1800.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2SC
Point Name: BIG2SC
Point Type: LDO
Descriptor: R121F S RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 10 01
Inverted: No
********************************************************************************
Point System Name: BIG2SI
Point Name: BIG2SI
Point Type: LAO
Descriptor: 2 SOLAR SHADE HI
Value: 30000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
********************************************************************************
Point System Name: BIG2SO
Point Name: BIG2SO
Point Type: LDO
Descriptor: R121F S RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 10 02
Inverted: No
********************************************************************************
Point System Name: BIG2SV
Point Name: BIG2SV
Point Type: LAO
Descriptor: SO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG2TD
Point Name: BIG2TD
Point Type: LAI
Descriptor: SETPT DEV
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 0.25
********************************************************************************
Point System Name: BIG2TO
Point Name: BIG2TO
Point Type: LAI
Descriptor: TABLE OUTPUT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG2V1
Point Name: BIG2V1
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2V2
Point Name: BIG2V2
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2V3
Point Name: BIG2V3
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2V4
Point Name: BIG2V4
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2V5
Point Name: BIG2V5
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2V6
Point Name: BIG2V6
Point Type: LDO
Descriptor: VNT CNT SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG2ZC
Point Name: BIG2ZC
Point Type: LAI
Descriptor: ROOM TEMPSET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.CLOSE.SHADE.HEAT
Point Name: BIG3.CLOSE.SHADE.HEAT
Point Type: LDO
Descriptor: HEAT CONSERV
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.CLOSE.SHADE.LITE
Point Name: BIG3.CLOSE.SHADE.LITE
Point Type: LDO
Descriptor: DRAPE CLOSE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.CLOSE.SHADES
Point Name: BIG3.CLOSE.SHADES
Point Type: LDO
Descriptor: SHADE SWITCH
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.CO2
Point Name: BIG3.CO2
Point Type: LAI
Descriptor: R121G CO2
Value: -500.0
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.08138
Intercept: -499.99997
COV Limit: 10.0
********************************************************************************
Point System Name: BIG3.DAY.LITE.LVL
Point Name: BIG3.DAY.LITE.LVL
Point Type: LAO
Descriptor: DAY EXT LVL
Value: 4000.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.DAY.MODE
Point Name: BIG3.DAY.MODE
Point Type: LDO
Descriptor: DAY MODE SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.DAY.RMS
Point Name: BIG3.DAY.RMS
Point Type: LAO
Descriptor: DAY TEMP SET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.EF.FAST.ENA
Point Name: BIG3.EF.FAST.ENA
Point Type: LDO
Descriptor: EXH FAN FAST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.EF.FAST.SS
Point Name: BIG3.EF.FAST.SS
Point Type: LDO
Descriptor: EXH FAN FAST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 06 06
Inverted: No
********************************************************************************
Point System Name: BIG3.EF.SLOW.ENA
Point Name: BIG3.EF.SLOW.ENA
Point Type: LDO
Descriptor: EXH FAN SLOW
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.EF.SLOW.SS
Point Name: BIG3.EF.SLOW.SS
Point Type: LDO
Descriptor: EXH FAN SLOW
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 06 05
Inverted: No
********************************************************************************
Point System Name: BIG3.FAN.LOCKOUT
Point Name: BIG3.FAN.LOCKOUT
Point Type: LDO
Descriptor: FAN LOCKOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.HID.LITES
Point Name: BIG3.HID.LITES
Point Type: LDO
Descriptor: HID LITES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 04 05
Inverted: No
********************************************************************************
Point System Name: BIG3.HIGH.INT.LITE.DELAY
Point Name: BIG3.HIGH.INT.LITE.DELAY
Point Type: LAO
Descriptor: TIME DELAY
Value: 1.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: MINUTE
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.INC.LITES
Point Name: BIG3.INC.LITES
Point Type: LDO
Descriptor: INCAN LITES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 04 06
Inverted: No
********************************************************************************
Point System Name: BIG3.LITE.HID.ENA
Point Name: BIG3.LITE.HID.ENA
Point Type: LDO
Descriptor: HID DBSWIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.LITE.INC.ENA
Point Name: BIG3.LITE.INC.ENA
Point Type: LDO
Descriptor: INC DBSWIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.LITE.INTENSITY
Point Name: BIG3.LITE.INTENSITY
Point Type: LAO
Descriptor: LITE INTSTY
Value: 5302.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 30.21333
********************************************************************************
Point System Name: BIG3.LOOP.MAX
Point Name: BIG3.LOOP.MAX
Point Type: LAO
Descriptor: LOOP MAX OUT
Value: 99.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.LOOPOUT
Point Name: BIG3.LOOPOUT
Point Type: LAO
Descriptor: TEMP LOOPOUT
Value: 80.51
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.MAN.VENT.LOCK
Point Name: BIG3.MAN.VENT.LOCK
Point Type: LDO
Descriptor: VENT LOCKOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.N.VENT.CLOSE
Point Name: BIG3.N.VENT.CLOSE
Point Type: LDO
Descriptor: NO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.NITE.RMS
Point Name: BIG3.NITE.RMS
Point Type: LAO
Descriptor: NGT TEMP SET
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.PUMP.LOCKOUT
Point Name: BIG3.PUMP.LOCKOUT
Point Type: LAO
Descriptor: PUMP LOCKOUT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.PUMP.SS
Point Name: BIG3.PUMP.SS
Point Type: LDO
Descriptor: R121G PUMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: HULINGS.PXCM32
Point Address: 0 07 03
Inverted: No
********************************************************************************
Point System Name: BIG3.RAD.HIGH
Point Name: BIG3.RAD.HIGH
Point Type: LAO
Descriptor: R121G RAD HI
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIG3.RAD.LOW
Point Name: BIG3.RAD.LOW
Point Type: LAO
Descriptor: R121G RAD LO
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 08
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: BIG3.RMH
Point Name: BIG3.RMH
Point Type: LAI
Descriptor: R121G HUMID
Value: 6.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT RH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.99829
COV Limit: 3.0
********************************************************************************
Point System Name: BIG3.RMS
Point Name: BIG3.RMS
Point Type: LAI
Descriptor: ROOM TEMPSET
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.RMT
Point Name: BIG3.RMT
Point Type: LAI
Descriptor: R121G ZN TMP
Value: 74.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Enhanced Alarms
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 01 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -3.887
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3.S.VENT.CLOSE
Point Name: BIG3.S.VENT.CLOSE
Point Type: LDO
Descriptor: SO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.VENT.RESET
Point Name: BIG3.VENT.RESET
Point Type: LDI
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 1 03 94
Normally Closed: No
********************************************************************************
Point System Name: BIG3.VENT.REST
Point Name: BIG3.VENT.REST
Point Type: LDO
Descriptor: VENT RESET
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.VENT.SKIP
Point Name: BIG3.VENT.SKIP
Point Type: LDO
Descriptor: VENT SKIP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3.WATTS.METER
Point Name: BIG3.WATTS.METER
Point Type: LAI
Descriptor: WATTSQMTR
Value: 85.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: WSQMTR
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.053341
Intercept: -327.72491
COV Limit: 1.02414
********************************************************************************
Point System Name: BIG301
Point Name: BIG301
Point Type: LDO
Descriptor: RESET TOGGLE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG302
Point Name: BIG302
Point Type: LDO
Descriptor: SV OPEN QTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG303
Point Name: BIG303
Point Type: LDO
Descriptor: SV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG304
Point Name: BIG304
Point Type: LDO
Descriptor: SV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG305
Point Name: BIG305
Point Type: LDO
Descriptor: SV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG306
Point Name: BIG306
Point Type: LDO
Descriptor: SV CLOSE QTR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG307
Point Name: BIG307
Point Type: LDO
Descriptor: SV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG308
Point Name: BIG308
Point Type: LDO
Descriptor: NV OPEN QTR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG309
Point Name: BIG309
Point Type: LDO
Descriptor: NV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG310
Point Name: BIG310
Point Type: LDO
Descriptor: NV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG311
Point Name: BIG311
Point Type: LDO
Descriptor: NV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG312
Point Name: BIG312
Point Type: LDO
Descriptor: NV CLOSE QTR
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG313
Point Name: BIG313
Point Type: LDO
Descriptor: NV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG314
Point Name: BIG314
Point Type: LDO
Descriptor: LV OPEN HALF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG315
Point Name: BIG315
Point Type: LDO
Descriptor: LV OPEN FULL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG316
Point Name: BIG316
Point Type: LDO
Descriptor: LV CLOSE HLF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG317
Point Name: BIG317
Point Type: LDO
Descriptor: LV CLOSE FUL
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG318
Point Name: BIG318
Point Type: LAO
Descriptor: 3 SOLAR SHADE LO
Value: 25000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
********************************************************************************
Point System Name: BIG320
Point Name: BIG320
Point Type: LDO
Descriptor: OPEN SLOW SW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3CL
Point Name: BIG3CL
Point Type: LDO
Descriptor: LO VENT CLOS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3DC
Point Name: BIG3DC
Point Type: LDO
Descriptor: R121G SHD CL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 05 06
Inverted: No
********************************************************************************
Point System Name: BIG3DO
Point Name: BIG3DO
Point Type: LDO
Descriptor: R121G SHD OP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 05 05
Inverted: No
********************************************************************************
Point System Name: BIG3HOLD1
Point Name: BIG3HOLD1
Point Type: LAO
Descriptor: HOLDER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MINUTE
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3HS
Point Name: BIG3HS
Point Type: LAO
Descriptor: H RAD SET ON
Value: 32.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3LC
Point Name: BIG3LC
Point Type: LDO
Descriptor: R121G S VENT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 09 05
Inverted: No
********************************************************************************
Point System Name: BIG3LH
Point Name: BIG3LH
Point Type: LDO
Descriptor: HID TOD SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3LL
Point Name: BIG3LL
Point Type: LDO
Descriptor: INC TOD SWT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3LO
Point Name: BIG3LO
Point Type: LDO
Descriptor: R121G S VENT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 09 06
Inverted: No
********************************************************************************
Point System Name: BIG3LV
Point Name: BIG3LV
Point Type: LAO
Descriptor: LO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG3NC
Point Name: BIG3NC
Point Type: LDO
Descriptor: R121G N RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 10 05
Inverted: No
********************************************************************************
Point System Name: BIG3NO
Point Name: BIG3NO
Point Type: LDO
Descriptor: R121G N RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 10 06
Inverted: No
********************************************************************************
Point System Name: BIG3NV
Point Name: BIG3NV
Point Type: LAO
Descriptor: NO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG3PS
Point Name: BIG3PS
Point Type: LAO
Descriptor: PHOTO SYN LV
Value: 12000.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3RV
Point Name: BIG3RV
Point Type: LAO
Descriptor: VENT SETTING
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG3S1
Point Name: BIG3S1
Point Type: LAO
Descriptor: SECNDS
Value: 155.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S2
Point Name: BIG3S2
Point Type: LAO
Descriptor: SECNDS
Value: 1200.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S3
Point Name: BIG3S3
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S4
Point Name: BIG3S4
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S5
Point Name: BIG3S5
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S6
Point Name: BIG3S6
Point Type: LAO
Descriptor: SECNDS
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S7
Point Name: BIG3S7
Point Type: LAO
Descriptor: SECNDS
Value: 1005.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S8
Point Name: BIG3S8
Point Type: LAO
Descriptor: SECNDS
Value: 155.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3S9
Point Name: BIG3S9
Point Type: LAO
Descriptor: SECNDS
Value: 1800.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIG3SC
Point Name: BIG3SC
Point Type: LDO
Descriptor: R121G S RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 10 03
Inverted: No
********************************************************************************
Point System Name: BIG3SI
Point Name: BIG3SI
Point Type: LAO
Descriptor: 3 SOLAR SHADE HI
Value: 30000.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 3.0
********************************************************************************
Point System Name: BIG3SO
Point Name: BIG3SO
Point Type: LDO
Descriptor: R121G S RVNT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 10 04
Inverted: No
********************************************************************************
Point System Name: BIG3SV
Point Name: BIG3SV
Point Type: LAO
Descriptor: SO VENT SET
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.2
********************************************************************************
Point System Name: BIG3V1
Point Name: BIG3V1
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3V2
Point Name: BIG3V2
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3V3
Point Name: BIG3V3
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3V4
Point Name: BIG3V4
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3V5
Point Name: BIG3V5
Point Type: LDO
Descriptor: VNT CTL SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIG3V6
Point Name: BIG3V6
Point Type: LDO
Descriptor: VNT CNT SWT
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIGALM
Point Name: BIGALM
Point Type: LDO
Descriptor: GH CRIT ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
********************************************************************************
Point System Name: BIGCON
Point Name: BIGCON
Point Type: LDO
Descriptor: CAB 32 CNECT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 17 06
Inverted: No
********************************************************************************
Point System Name: BIGCTD
Point Name: BIGCTD
Point Type: LDO
Descriptor: CONNECT TDLY
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
********************************************************************************
Point System Name: BIGCTM
Point Name: BIGCTM
Point Type: LDO
Descriptor: CONNECT TMR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
********************************************************************************
Point System Name: BIGHAL
Point Name: BIGHAL
Point Type: LDI
Descriptor: GHSE TMP ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 05
Normally Closed: No
********************************************************************************
Point System Name: BIGNAL
Point Name: BIGNAL
Point Type: LDO
Descriptor: GHSE NET ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 07 06
Inverted: No
********************************************************************************
Point System Name: BIGOAT
Point Name: BIGOAT
Point Type: LAI
Descriptor: OUTSIDE TEMP
Value: 64.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 01 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.93998
COV Limit: 0.996
********************************************************************************
Point System Name: BIGOWM
Point Name: BIGOWM
Point Type: LAI
Descriptor: SOLAR SENSOR
Value: 513.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: WSQMTR
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 02 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.056461
Intercept: -346.89969
COV Limit: 1.02986
********************************************************************************
Point System Name: BIGSLR
Point Name: BIGSLR
Point Type: LAO
Descriptor: LITE INTSTY
Value: 31888.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: FTCNDL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 30.21333
********************************************************************************
Point System Name: BIGWDD
Point Name: BIGWDD
Point Type: LAI
Descriptor: WIND DIRECT
Value: -90.0
Condition: *F*
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.014649
Intercept: -90.00143
COV Limit: 0.99847
********************************************************************************
Point System Name: BIGWDS
Point Name: BIGWDS
Point Type: LAI
Descriptor: WIND SPEED
Value: 57.42
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: MILEHR
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM32
Point Address: 0 03 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.006991
Intercept: -42.95014
COV Limit: 1.99988
********************************************************************************
Point System Name: BIHD01
Point Name: BIHD01
Point Type: LDI
Descriptor: B02 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 01
Normally Closed: No
********************************************************************************
Point System Name: BIHD02
Point Name: BIHD02
Point Type: LDI
Descriptor: B02A HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 02
Normally Closed: No
********************************************************************************
Point System Name: BIHD03
Point Name: BIHD03
Point Type: LDI
Descriptor: B03 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 03
Normally Closed: No
********************************************************************************
Point System Name: BIHD04
Point Name: BIHD04
Point Type: LDI
Descriptor: B33 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 04
Normally Closed: No
********************************************************************************
Point System Name: BIHD05
Point Name: BIHD05
Point Type: LDI
Descriptor: 102 HOOD NO.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 05
Normally Closed: No
********************************************************************************
Point System Name: BIHD07
Point Name: BIHD07
Point Type: LDI
Descriptor: 109 HOOD NW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 06
Normally Closed: No
********************************************************************************
Point System Name: BIHD09
Point Name: BIHD09
Point Type: LDI
Descriptor: 109 HOOD SW.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 07
Normally Closed: No
********************************************************************************
Point System Name: BIHD11
Point Name: BIHD11
Point Type: LDI
Descriptor: 111 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 08
Normally Closed: No
********************************************************************************
Point System Name: BIHD13
Point Name: BIHD13
Point Type: LDI
Descriptor: 112 HOOD NW.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 09
Normally Closed: No
********************************************************************************
Point System Name: BIHD15
Point Name: BIHD15
Point Type: LDI
Descriptor: 112 HOOD SE.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 10
Normally Closed: No
********************************************************************************
Point System Name: BIHD16
Point Name: BIHD16
Point Type: LDI
Descriptor: 121 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 11
Normally Closed: No
********************************************************************************
Point System Name: BIHD17
Point Name: BIHD17
Point Type: LDI
Descriptor: 121B HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 12
Normally Closed: No
********************************************************************************
Point System Name: BIHD18
Point Name: BIHD18
Point Type: LDI
Descriptor: 202 HOOD NE.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 13
Normally Closed: No
********************************************************************************
Point System Name: BIHD21
Point Name: BIHD21
Point Type: LDI
Descriptor: 203 HOOD SW.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 14
Normally Closed: No
********************************************************************************
Point System Name: BIHD22
Point Name: BIHD22
Point Type: LDI
Descriptor: 203A HOOD NW
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 15
Normally Closed: No
********************************************************************************
Point System Name: BIHD24
Point Name: BIHD24
Point Type: LDI
Descriptor: 206 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 01 16
Normally Closed: No
********************************************************************************
Point System Name: BIHD25
Point Name: BIHD25
Point Type: LDI
Descriptor: 207 HOOD NO.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 01
Normally Closed: No
********************************************************************************
Point System Name: BIHD26
Point Name: BIHD26
Point Type: LDI
Descriptor: 207 HOOD MDL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 02
Normally Closed: No
********************************************************************************
Point System Name: BIHD30
Point Name: BIHD30
Point Type: LDI
Descriptor: 212 HOOD SW.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 03
Normally Closed: No
********************************************************************************
Point System Name: BIHD31
Point Name: BIHD31
Point Type: LDI
Descriptor: 212 HOOD SE.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 04
Normally Closed: No
********************************************************************************
Point System Name: BIHD32
Point Name: BIHD32
Point Type: LDI
Descriptor: 213 HOOD SE.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 05
Normally Closed: No
********************************************************************************
Point System Name: BIHD33
Point Name: BIHD33
Point Type: LDI
Descriptor: 215 HOOD NW.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 06
Normally Closed: No
********************************************************************************
Point System Name: BIHD35
Point Name: BIHD35
Point Type: LDI
Descriptor: 218 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 07
Normally Closed: No
********************************************************************************
Point System Name: BIHD36
Point Name: BIHD36
Point Type: LDI
Descriptor: 301 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 08
Normally Closed: No
********************************************************************************
Point System Name: BIHD37
Point Name: BIHD37
Point Type: LDI
Descriptor: 302 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 09
Normally Closed: No
********************************************************************************
Point System Name: BIHD38
Point Name: BIHD38
Point Type: LDI
Descriptor: 307 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 10
Normally Closed: No
********************************************************************************
Point System Name: BIHD39
Point Name: BIHD39
Point Type: LDI
Descriptor: 310 HOOD NO.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 11
Normally Closed: No
********************************************************************************
Point System Name: BIHD41
Point Name: BIHD41
Point Type: LDI
Descriptor: 315 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 12
Normally Closed: No
********************************************************************************
Point System Name: BIHD43
Point Name: BIHD43
Point Type: LDI
Descriptor: 319 HOOD SO.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 13
Normally Closed: No
********************************************************************************
Point System Name: BIHD44
Point Name: BIHD44
Point Type: LDI
Descriptor: 320 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 14
Normally Closed: No
********************************************************************************
Point System Name: BIHD46
Point Name: BIHD46
Point Type: LDI
Descriptor: 326 HOOD SO.
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 15
Normally Closed: No
********************************************************************************
Point System Name: BIHD47
Point Name: BIHD47
Point Type: LDI
Descriptor: 327 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 02 16
Normally Closed: No
********************************************************************************
Point System Name: BIHD48
Point Name: BIHD48
Point Type: LDI
Descriptor: 329 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 08 02
Normally Closed: No
********************************************************************************
Point System Name: BIHD49
Point Name: BIHD49
Point Type: LDI
Descriptor: 334 HOOD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 08 03
Normally Closed: No
********************************************************************************
Point System Name: BIHEATTAPE
Point Name: BIHEATTAPE
Point Type: LDO
Descriptor: HEAT.TAPES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 06 06
Inverted: No
********************************************************************************
Point System Name: BIHEATTAPE2
Point Name: BIHEATTAPE2
Point Type: LDO
Descriptor: HEAT.TAPES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 17 05
Inverted: No
********************************************************************************
Point System Name: BIHP1A
Point Name: BIHP1A
Point Type: LDO
Descriptor: HW PMP 1 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHP1S
Point Name: BIHP1S
Point Type: L2SL
Descriptor: HWP1 STRT ST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM30
On/Off Point Address: 0 05 01
Inverted: No
Proof Point Address: 0 08 04
Normally Closed: No
Proof Delay: 90 Informational Text
********************************************************************************
Point System Name: BIHP1V
Point Name: BIHP1V
Point Type: LAO
Descriptor: HP1 SPD CTRL
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 04 07
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BIHP2A
Point Name: BIHP2A
Point Type: LDO
Descriptor: HW PMP 2 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHP2S
Point Name: BIHP2S
Point Type: L2SL
Descriptor: HWP2 STRT ST
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM30
On/Off Point Address: 0 05 02
Inverted: No
Proof Point Address: 0 08 05
Normally Closed: No
Proof Delay: 90 Informational Text
********************************************************************************
Point System Name: BIHP2V
Point Name: BIHP2V
Point Type: LAO
Descriptor: HP2 SPD CTRL
Value: 7.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: VOLTS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 04 08
Actuator Type Voltage
Slope: 0.000326
Intercept: 0.0
COV Limit: 0.99984
********************************************************************************
Point System Name: BIHP4A
Point Name: BIHP4A
Point Type: LDO
Descriptor: HR PMP 4 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHP4S
Point Name: BIHP4S
Point Type: L2SL
Descriptor: HP4 STRT STP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 06 03
Inverted: No
Proof Point Address: 0 01 06
Normally Closed: No
Proof Delay: 10 Informational Text
********************************************************************************
Point System Name: BIHP5A
Point Name: BIHP5A
Point Type: LDO
Descriptor: HR PMP 5 ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHP5S
Point Name: BIHP5S
Point Type: L2SL
Descriptor: HP5 STRT STP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: HULINGS.PXCM27
On/Off Point Address: 0 06 04
Inverted: No
Proof Point Address: 0 01 07
Normally Closed: No
Proof Delay: 10 Informational Text
********************************************************************************
Point System Name: BIHRAL
Point Name: BIHRAL
Point Type: LDO
Descriptor: PUMP ALM RST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHREN
Point Name: BIHREN
Point Type: LDO
Descriptor: HEAT REC ENB
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHRPD
Point Name: BIHRPD
Point Type: LAO
Descriptor: HR PMP DELAY
Value: 30.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECNDS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIHRRT
Point Name: BIHRRT
Point Type: LAI
Descriptor: HRC SPLY TEM
Value: 72.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BIHRSQ
Point Name: BIHRSQ
Point Type: LDO
Descriptor: HR PMP SEQ
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHRST
Point Name: BIHRST
Point Type: LAI
Descriptor: HRC SPLY TEM
Value: 72.12
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: 0 08 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BIHTCL
Point Name: BIHTCL
Point Type: LDO
Descriptor: HEA CE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 17 04
Inverted: No
********************************************************************************
Point System Name: BIHTMD
Point Name: BIHTMD
Point Type: LDO
Descriptor: BI HTG MODE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHWAL
Point Name: BIHWAL
Point Type: LDO
Descriptor: PUMP ALM RST
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHWDC
Point Name: BIHWDC
Point Type: LAO
Descriptor: HW D PSI SET
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIHWDP
Point Name: BIHWDP
Point Type: LAI
Descriptor: HW SYS DP
Value: 415.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.040691
Intercept: -250.00139
COV Limit: 1.01564
********************************************************************************
Point System Name: BIHWDS
Point Name: BIHWDS
Point Type: LAO
Descriptor: LOOP PSI SET
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIHWEN
Point Name: BIHWEN
Point Type: LDO
Descriptor: HEAT ENABLE
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHWPR
Point Name: BIHWPR
Point Type: LAO
Descriptor: HEAT DIF PRS
Value: 15.27
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Standard Alarms
High Limit: 18.0
Low Limit: 12.0
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIHWRT
Point Name: BIHWRT
Point Type: LAI
Descriptor: HWR TEMP
Value: 128.06
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BIHWSC
Point Name: BIHWSC
Point Type: LAO
Descriptor: HW TEMP SET
Value: 140.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIHWSQ
Point Name: BIHWSQ
Point Type: LDO
Descriptor: HW VIR TOGGL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
********************************************************************************
Point System Name: BIHWST
Point Name: BIHWST
Point Type: LAI
Descriptor: HWS TEMP
Value: 140.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Enhanced Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BILABA
Point Name: BILABA
Point Type: LDI
Descriptor: LAB AIR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 06
Normally Closed: No
********************************************************************************
Point System Name: BIOAT27
Point Name: BIOAT27
Point Type: LAO
Descriptor: OATEMP
Value: 61.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM27
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIOAT28
Point Name: BIOAT28
Point Type: LAO
Descriptor: OATEMP
Value: 61.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIOAT29
Point Name: BIOAT29
Point Type: LAO
Descriptor: OATEMP
Value: 61.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM29
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIOAT30
Point Name: BIOAT30
Point Type: LAO
Descriptor: OATEMP
Value: 61.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIP3DT
Point Name: BIP3DT
Point Type: LAO
Descriptor: DAY TMP SP
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIP3NT
Point Name: BIP3NT
Point Type: LAO
Descriptor: NITE TMP SP
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIP4DT
Point Name: BIP4DT
Point Type: LAO
Descriptor: DAY TMP SP
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIP4NT
Point Name: BIP4NT
Point Type: LAO
Descriptor: NITE TMP SP
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIP5DT
Point Name: BIP5DT
Point Type: LAO
Descriptor: DAY TMP SP
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIP5NT
Point Name: BIP5NT
Point Type: LAO
Descriptor: NITE TMP SP
Value: 75.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: BIPRG1
Point Name: BIPRG1
Point Type: LDO
Descriptor: SMK PRG FLR1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 17 01
Inverted: No
********************************************************************************
Point System Name: BIPRG2
Point Name: BIPRG2
Point Type: LDO
Descriptor: SMK PRG FLR2
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 17 02
Inverted: No
********************************************************************************
Point System Name: BIPRG3
Point Name: BIPRG3
Point Type: LDO
Descriptor: SMK PRG FLR3
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 17 03
Inverted: No
********************************************************************************
Point System Name: BIPU3A
Point Name: BIPU3A
Point Type: LDI
Descriptor: LIEBERT UNIT 3
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 09
Normally Closed: No
********************************************************************************
Point System Name: BIPU4A
Point Name: BIPU4A
Point Type: LDI
Descriptor: LIEBERT UNIT 4
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 08
Normally Closed: No
********************************************************************************
Point System Name: BIPU5A
Point Name: BIPU5A
Point Type: LDI
Descriptor: LIEBERT UINT 5
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 10 07
Normally Closed: No
********************************************************************************
Point System Name: BIS17C
Point Name: BIS17C
Point Type: LDO
Descriptor: E17 DPR CLOS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 18 05
Inverted: No
********************************************************************************
Point System Name: BIS17L
Point Name: BIS17L
Point Type: LDO
Descriptor: EF17 LITES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 18 03
Inverted: No
********************************************************************************
Point System Name: BIS17O
Point Name: BIS17O
Point Type: LDO
Descriptor: E17 DPR OPEN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 18 06
Inverted: No
********************************************************************************
Point System Name: BIS18C
Point Name: BIS18C
Point Type: LDO
Descriptor: E18 DPR CLOS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 19 04
Inverted: No
********************************************************************************
Point System Name: BIS18L
Point Name: BIS18L
Point Type: LDO
Descriptor: EF18 LITES
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 19 02
Inverted: No
********************************************************************************
Point System Name: BIS18O
Point Name: BIS18O
Point Type: LDO
Descriptor: E18 DPR OPEN
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 19 01
Inverted: No
********************************************************************************
Point System Name: BISA1F
Point Name: BISA1F
Point Type: LDI
Descriptor: SMK AH1 OFF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 02
Normally Closed: No
********************************************************************************
Point System Name: BISA1L
Point Name: BISA1L
Point Type: LDO
Descriptor: AH1 LITES
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 18 02
Inverted: No
********************************************************************************
Point System Name: BISA1O
Point Name: BISA1O
Point Type: LDI
Descriptor: SMK AH1 ON
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 01
Normally Closed: No
********************************************************************************
Point System Name: BISA2F
Point Name: BISA2F
Point Type: LDI
Descriptor: SMK AH2 OFF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 04
Normally Closed: No
********************************************************************************
Point System Name: BISA2L
Point Name: BISA2L
Point Type: LDO
Descriptor: AH2 LITES
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 18 01
Inverted: No
********************************************************************************
Point System Name: BISA2O
Point Name: BISA2O
Point Type: LDI
Descriptor: SMK AH2 ON
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 03
Normally Closed: No
********************************************************************************
Point System Name: BISA3F
Point Name: BISA3F
Point Type: LDI
Descriptor: SMK AH3 OFF
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 06
Normally Closed: No
********************************************************************************
Point System Name: BISA3L
Point Name: BISA3L
Point Type: LDO
Descriptor: AH3 LITES
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 18 04
Inverted: No
********************************************************************************
Point System Name: BISA3O
Point Name: BISA3O
Point Type: LDI
Descriptor: SMK AH3 ON
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 05
Normally Closed: No
********************************************************************************
Point System Name: BISE17
Point Name: BISE17
Point Type: LDI
Descriptor: SMK EF17 ON
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 07
Normally Closed: No
********************************************************************************
Point System Name: BISE18
Point Name: BISE18
Point Type: LDI
Descriptor: SMK EF18 ON
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 08
Normally Closed: No
********************************************************************************
Point System Name: BISELL
Point Name: BISELL
Point Type: LDO
Descriptor: ELEV DPR LIT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 19 03
Inverted: No
********************************************************************************
Point System Name: BISELO
Point Name: BISELO
Point Type: LDI
Descriptor: SMK ELV DPR
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 09
Normally Closed: No
********************************************************************************
Point System Name: BISMP1
Point Name: BISMP1
Point Type: LDI
Descriptor: SEWAGE SUMP1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 13
Normally Closed: No
********************************************************************************
Point System Name: BISMP2
Point Name: BISMP2
Point Type: LDI
Descriptor: SEWAGE SUMP2
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 14
Normally Closed: No
********************************************************************************
Point System Name: BISMP3
Point Name: BISMP3
Point Type: LDI
Descriptor: ELEV SUMP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 15
Normally Closed: No
********************************************************************************
Point System Name: BISPG1
Point Name: BISPG1
Point Type: LDI
Descriptor: SMK PRG FLR1
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 10
Normally Closed: No
********************************************************************************
Point System Name: BISPG2
Point Name: BISPG2
Point Type: LDI
Descriptor: SMK PRG FLR2
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 11
Normally Closed: No
********************************************************************************
Point System Name: BISPG3
Point Name: BISPG3
Point Type: LDI
Descriptor: SMK PRG FLR3
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 11 12
Normally Closed: No
********************************************************************************
Point System Name: BIVACA
Point Name: BIVACA
Point Type: LDI
Descriptor: VAC PMP ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: HULINGS.PXCM28
Point Address: 0 01 05
Normally Closed: No
********************************************************************************
Point System Name: BIZ01H
Point Name: BIZ01H
Point Type: LAI
Descriptor: B17 HUMID
Value: 14.79
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -22.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ01T
Point Name: BIZ01T
Point Type: LAI
Descriptor: B17 TEMP
Value: 74.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 89.97
Low Limit: 50.0
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -0.46
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ02H
Point Name: BIZ02H
Point Type: LAI
Descriptor: B20 HUMID
Value: 25.87
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ02T
Point Name: BIZ02T
Point Type: LAI
Descriptor: B20 TEMP
Value: 76.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ03H
Point Name: BIZ03H
Point Type: LAI
Descriptor: B20A HUMID
Value: 27.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ03T
Point Name: BIZ03T
Point Type: LAI
Descriptor: B20A TEMP
Value: 73.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 04
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ04H
Point Name: BIZ04H
Point Type: LAI
Descriptor: B20B HUMID
Value: 22.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ04T
Point Name: BIZ04T
Point Type: LAI
Descriptor: B20B TEMP
Value: 80.47
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ05H
Point Name: BIZ05H
Point Type: LAI
Descriptor: B20C HUMID
Value: 17.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ05T
Point Name: BIZ05T
Point Type: LAI
Descriptor: B20C TEMP
Value: 78.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 04 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ06H
Point Name: BIZ06H
Point Type: LAI
Descriptor: B21 HUMID
Value: 13.82
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ06T
Point Name: BIZ06T
Point Type: LAI
Descriptor: B21 TEMP
Value: 73.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 04 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.46
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ07H
Point Name: BIZ07H
Point Type: LAI
Descriptor: B27 HUMID
Value: 10.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -87.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ07T
Point Name: BIZ07T
Point Type: LAI
Descriptor: B27 TEMP
Value: 75.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 2.54
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ08H
Point Name: BIZ08H
Point Type: LAI
Descriptor: B31 HUMID
Value: 11.89
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -80.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ08T
Point Name: BIZ08T
Point Type: LAI
Descriptor: B31 TEMP
Value: 70.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 84.97
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.33
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ09H
Point Name: BIZ09H
Point Type: LAI
Descriptor: B35 HUMID
Value: 14.32
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 07 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -26.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ09T
Point Name: BIZ09T
Point Type: LAI
Descriptor: B35 TEMP
Value: 73.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 03 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -1.46
COV Limit: 0.996
********************************************************************************
Point System Name: BIZ10H
Point Name: BIZ10H
Point Type: LAI
Descriptor: B37 HUMID
Value: 17.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 08 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -38.99929
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ10T
Point Name: BIZ10T
Point Type: LAI
Descriptor: B37 TEMP
Value: 72.8
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 81.99
Low Limit: 60.0
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 01
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 1.0
********************************************************************************
Point System Name: BIZ11H
Point Name: BIZ11H
Point Type: LAI
Descriptor: 201 HUMID
Value: 73.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 08 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ11T
Point Name: BIZ11T
Point Type: LAI
Descriptor: RM201 WALKIN CLR
Value: 44.36
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 50.0
Low Limit: 35.0
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 02
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 1.0
********************************************************************************
Point System Name: BIZ12H
Point Name: BIZ12H
Point Type: LAI
Descriptor: 314 HUMID
Value: 77.21
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 08 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ12T
Point Name: BIZ12T
Point Type: LAI
Descriptor: RM314 WALKIN CLR
Value: 47.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 52.99
Low Limit: 34.98
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 06 03
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 1.0
********************************************************************************
Point System Name: BIZ13H
Point Name: BIZ13H
Point Type: LAI
Descriptor: B05 HUMID
Value: 41.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ13T
Point Name: BIZ13T
Point Type: LAI
Descriptor: B05 TEMP
Value: 78.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 06
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: 1.67
COV Limit: 1.0
********************************************************************************
Point System Name: BIZ14H
Point Name: BIZ14H
Point Type: LAI
Descriptor: B119 HUMID
Value: 30.32
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ14T
Point Name: BIZ14T
Point Type: LAI
Descriptor: 119 GROWTH RM
Value: 71.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 50.0
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 05
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.46
COV Limit: 1.0
********************************************************************************
Point System Name: BIZ15H
Point Name: BIZ15H
Point Type: LAI
Descriptor: 121A HUMID
Value: 30.61
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -24.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ15T
Point Name: BIZ15T
Point Type: LAI
Descriptor: 121A GROWTH RM
Value: 71.77
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 85.0
Low Limit: 45.0
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 08
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 1.0
Intercept: -2.46
COV Limit: 1.0
********************************************************************************
Point System Name: BIZ16H
Point Name: BIZ16H
Point Type: LAI
Descriptor: 119 HUMID
Value: 22.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -18.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: BIZ16T
Point Name: BIZ16T
Point Type: LAI
Descriptor: B19 TEMP
Value: 78.62
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: HULINGS.PXCM30
Point Address: 0 13 07
Sensor Type: MEC RTD
Wire Resistance: 0.0
Slope: 0.99498
Intercept: 1.54
COV Limit: 1.0
********************************************************************************
******************************** End of Report *********************************

## Sayles
10/16/2017 Carleton College 02:57 PM
Panel Point Definition Report
Selection: SH.GENRUN, SH.PNL05.SHEDTMR, SH.STEAM.DEMAND, sh.test.pt, ...
(113 Points)
Point System Name: SH.GENRUN
Point Name: SH.GENRUN
Point Type: LDO
Descriptor:
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 09 05
Inverted: No
********************************************************************************
Point System Name: SH.PNL05.SHEDTMR
Point Name: SH.PNL05.SHEDTMR
Point Type: LAO
Descriptor:
Value: 27121940.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SH.STEAM.DEMAND
Point Name: SH.STEAM.DEMAND
Point Type: LAI
Descriptor: STEAM DEMAND
Value: -0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM/HR
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: SAYLES.HILL
Point Address: 0 03 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.160238
Intercept: -984.49994
COV Limit: 50.0
********************************************************************************
Point System Name: sh.test.pt
Point Name: sh.test.pt
Point Type: LDO
Descriptor: test
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SH4RF1
Point Name: SH4RF1
Point Type: LDO
Descriptor: AHU4 RELEF 1
Value: ON
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 08 06
Inverted: No
********************************************************************************
Point System Name: SH4RF2
Point Name: SH4RF2
Point Type: LDO
Descriptor: AHU4 RELEF 2
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 09 04
Inverted: No
********************************************************************************
Point System Name: SHA1DA
Point Name: SHA1DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 64.3
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 03 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA1DC
Point Name: SHA1DC
Point Type: LAO
Descriptor: MIX AIR DMP
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA1DM
Point Name: SHA1DM
Point Type: LAO
Descriptor: SFN DMP MIN
Value: 6.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA1DS
Point Name: SHA1DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA1DV
Point Name: SHA1DV
Point Type: LAO
Descriptor: DISCH CNTRL
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA1MS
Point Name: SHA1MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 57.64
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA1MT
Point Name: SHA1MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 67.68
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 95.0
Low Limit: 32.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 2.0
********************************************************************************
Point System Name: SHA1OC
Point Name: SHA1OC
Point Type: LDO
Descriptor: AHU1 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SHA1PS
Point Name: SHA1PS
Point Type: LAO
Descriptor: STATIC SETPT
Value: 0.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA1RD
Point Name: SHA1RD
Point Type: LAO
Descriptor: REL IEF DMP
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 02 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA1RP
Point Name: SHA1RP
Point Type: LAI
Descriptor: RM PRESS
Value: 0.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WG
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 03 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00001
Intercept: -0.06316
COV Limit: 0.01
********************************************************************************
Point System Name: SHA1RS
Point Name: SHA1RS
Point Type: LAO
Descriptor: ROOM SETPNT
Value: 65.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA1SS
Point Name: SHA1SS
Point Type: L2SL
Descriptor: AHU 1 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: SAYLES.HILL
On/Off Point Address: 0 08 01
Inverted: No
Proof Point Address: 0 11 04
Normally Closed: No
Proof Delay: 300 Informational Text
********************************************************************************
Point System Name: SHA1ST
Point Name: SHA1ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 70.85
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 90.0
Low Limit: 50.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -10.00014
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2CD
Point Name: SHA2CD
Point Type: LAI
Descriptor: COLD DEK TMP
Value: 61.63
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 03 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2CS
Point Name: SHA2CS
Point Type: LAO
Descriptor: COOL SETPNT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA2CV
Point Name: SHA2CV
Point Type: LAO
Descriptor: COOL VL
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 08
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2DA
Point Name: SHA2DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 62.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 03 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2DC
Point Name: SHA2DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2DD
Point Name: SHA2DD
Point Type: LAO
Descriptor: DIS AIR DMPR
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 02 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2DS
Point Name: SHA2DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA2HD
Point Name: SHA2HD
Point Type: LAI
Descriptor: HOT DEK TEMP
Value: 65.15
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 03 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004883
Intercept: -0.00141
COV Limit: 0.99854
********************************************************************************
Point System Name: SHA2HS
Point Name: SHA2HS
Point Type: LAO
Descriptor: HOT DEK STPT
Value: 80.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA2HV
Point Name: SHA2HV
Point Type: LAO
Descriptor: HEAT VL
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2MS
Point Name: SHA2MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA2MT
Point Name: SHA2MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 65.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 10 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2OC
Point Name: SHA2OC
Point Type: LDO
Descriptor: AHU2 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SHA2S1
Point Name: SHA2S1
Point Type: LAI
Descriptor: SPACE TEMP
Value: 73.64
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 94.99
Low Limit: 50.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA2SS
Point Name: SHA2SS
Point Type: L2SL
Descriptor: AHU 2 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: SAYLES.HILL
On/Off Point Address: 0 08 02
Inverted: No
Proof Point Address: 0 11 05
Normally Closed: No
Proof Delay: 300 Informational Text
********************************************************************************
Point System Name: SHA3CV
Point Name: SHA3CV
Point Type: LAO
Descriptor: COOL VALVE
Value: 9.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA3DA
Point Name: SHA3DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 60.16
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 10 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA3DC
Point Name: SHA3DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA3DS
Point Name: SHA3DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA3HS
Point Name: SHA3HS
Point Type: LAO
Descriptor: HEAT SETPNT
Value: 50.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA3HV
Point Name: SHA3HV
Point Type: LAO
Descriptor: HEAT VALVE
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 02 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA3MS
Point Name: SHA3MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA3MT
Point Name: SHA3MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 63.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 95.0
Low Limit: 40.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 10 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -2.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA3OC
Point Name: SHA3OC
Point Type: LDO
Descriptor: AHU3 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SHA3RS
Point Name: SHA3RS
Point Type: LAO
Descriptor: ROOM SETPNT
Value: 68.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA3SS
Point Name: SHA3SS
Point Type: L2SL
Descriptor: AHU 3 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: SAYLES.HILL
On/Off Point Address: 0 08 03
Inverted: No
Proof Point Address: 0 11 06
Normally Closed: No
Proof Delay: 300 Informational Text
********************************************************************************
Point System Name: SHA3ST
Point Name: SHA3ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 68.04
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 94.99
Low Limit: 50.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 10 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -6.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA4.ELEV.OVRD
Point Name: SHA4.ELEV.OVRD
Point Type: LDO
Descriptor: ELEV RMT OVRD
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SHA4.MAX.DMPR.COMD
Point Name: SHA4.MAX.DMPR.COMD
Point Type: LAO
Descriptor:
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: %
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA4CV
Point Name: SHA4CV
Point Type: LAO
Descriptor: COOL VALVE
Value: 5.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 02 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA4DA
Point Name: SHA4DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 55.67
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 03 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA4DC
Point Name: SHA4DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 13.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 02 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA4DS
Point Name: SHA4DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA4FRZ
Point Name: SHA4FRZ
Point Type: LDI
Descriptor: AHU 4 FREEZE
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 11 07
Normally Closed: No
********************************************************************************
Point System Name: SHA4HV
Point Name: SHA4HV
Point Type: LAO
Descriptor: HEAT VALVE
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 01 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA4MS
Point Name: SHA4MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 52.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA4MT
Point Name: SHA4MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 69.35
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 95.0
Low Limit: 40.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 03 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: SHA4OC
Point Name: SHA4OC
Point Type: LDO
Descriptor: AHU4 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SHA4PS
Point Name: SHA4PS
Point Type: LAO
Descriptor: STATIC STPT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHA4SP
Point Name: SHA4SP
Point Type: LAI
Descriptor: DUCT STATIC
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN WG
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24912
COV Limit: 0.04992
********************************************************************************
Point System Name: SHA4SS
Point Name: SHA4SS
Point Type: L2SL
Descriptor: AHU 4 SS
Value: ON
Condition: -N-
Priority: OPER
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: SAYLES.HILL
On/Off Point Address: 3 01 24
Inverted: No
Proof Point Address: 3 01 23
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: SHCHWR
Point Name: SHCHWR
Point Type: LAI
Descriptor: CHWR TEMP
Value: 55.29
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.002034
Intercept: 7.50035
COV Limit: 0.99994
********************************************************************************
Point System Name: SHCHWS
Point Name: SHCHWS
Point Type: LAI
Descriptor: CHWS TEMP
Value: 46.33
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.002034
Intercept: 7.50035
COV Limit: 0.99994
********************************************************************************
Point System Name: SHCONV
Point Name: SHCONV
Point Type: LAO
Descriptor: HW CONV VLVE
Value: 8.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 02 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: SHCOSP
Point Name: SHCOSP
Point Type: LAO
Descriptor: CONV SETPNT
Value: 136.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHECON
Point Name: SHECON
Point Type: LDO
Descriptor: ECONOMIZE MD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SHEMTS
Point Name: SHEMTS
Point Type: LDI
Descriptor: SH EMER TS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 11 11
Normally Closed: No
********************************************************************************
Point System Name: SHFIRE
Point Name: SHFIRE
Point Type: LDI
Descriptor: FIRE ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 11 10
Normally Closed: No
********************************************************************************
Point System Name: SHHD01
Point Name: SHHD01
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD02
Point Name: SHHD02
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD03
Point Name: SHHD03
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD04
Point Name: SHHD04
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD05
Point Name: SHHD05
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD06
Point Name: SHHD06
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD07
Point Name: SHHD07
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD08
Point Name: SHHD08
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD09
Point Name: SHHD09
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD10
Point Name: SHHD10
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD11
Point Name: SHHD11
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD12
Point Name: SHHD12
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD13
Point Name: SHHD13
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD14
Point Name: SHHD14
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD15
Point Name: SHHD15
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD16
Point Name: SHHD16
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD17
Point Name: SHHD17
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD18
Point Name: SHHD18
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD19
Point Name: SHHD19
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD20
Point Name: SHHD20
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD21
Point Name: SHHD21
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD22
Point Name: SHHD22
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD23
Point Name: SHHD23
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD24
Point Name: SHHD24
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD25
Point Name: SHHD25
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD26
Point Name: SHHD26
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD27
Point Name: SHHD27
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD28
Point Name: SHHD28
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD29
Point Name: SHHD29
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD30
Point Name: SHHD30
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD31
Point Name: SHHD31
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD32
Point Name: SHHD32
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD33
Point Name: SHHD33
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD34
Point Name: SHHD34
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD35
Point Name: SHHD35
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD36
Point Name: SHHD36
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD37
Point Name: SHHD37
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHD38
Point Name: SHHD38
Point Type: LAO
Descriptor: RMS HOLD PNT
Value: 76.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: SHHWLD
Point Name: SHHWLD
Point Type: LDO
Descriptor: HW PMP LEAD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: -Virtual-
********************************************************************************
Point System Name: SHHWP1
Point Name: SHHWP1
Point Type: L2SL
Descriptor: HW PUMP 1 SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: SAYLES.HILL
On/Off Point Address: 0 09 01
Inverted: No
Proof Point Address: 0 11 08
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: SHHWP2
Point Name: SHHWP2
Point Type: L2SL
Descriptor: HW PUMP 2 SS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: SAYLES.HILL
On/Off Point Address: 0 09 02
Inverted: No
Proof Point Address: 0 11 09
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: SHHWRT
Point Name: SHHWRT
Point Type: LAI
Descriptor: HW RET TEMP
Value: 132.03
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.006103
Intercept: 32.50106
COV Limit: 1.00189
********************************************************************************
Point System Name: SHHWST
Point Name: SHHWST
Point Type: LAI
Descriptor: HW SUP TEMP
Value: 136.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Standard Alarms
High Limit: 210.0
Low Limit: 65.0
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 04 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.006103
Intercept: 32.50106
COV Limit: 1.00189
********************************************************************************
Point System Name: SHRDDN
Point Name: SHRDDN
Point Type: LDO
Descriptor: DAY NIT EP
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 09 03
Inverted: No
********************************************************************************
Point System Name: SHSBEF
Point Name: SHSBEF
Point Type: LDO
Descriptor: SNACK BAR EX
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: SAYLES.HILL
Point Address: 0 08 04
Inverted: No
********************************************************************************
******************************** End of Report *********************************

## Library
10/16/2017 Carleton College 02:53 PM
Panel Point Definition Report
Selection: LI RARE BOOK HUMIDITY, LI.4TH.FLR.RMH, LI.4TH.FLR.RMT, ...
(242 Points)
Point System Name: LI RARE BOOK HUMIDITY
Point Name: LI RARE BOOK HUMIDITY
Point Type: LAI
Descriptor: HUMIDITY
Value: 38.75
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: % RH
Alarm Type: Standard Alarms
High Limit: 50.0
Low Limit: 25.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 09 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.4TH.FLR.RMH
Point Name: LI.4TH.FLR.RMH
Point Type: LAI
Descriptor: 4TH FLR RMH
Value: 51.32
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: %
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 10 01
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.003906
Intercept: -14.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.4TH.FLR.RMT
Point Name: LI.4TH.FLR.RMT
Point Type: LAI
Descriptor: 4TH FLR RMT
Value: 74.18
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 10 02
Sensor Type: Voltage
Wire Resistance: 0.0
Slope: 0.001563
Intercept: 49.4
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.RAD420.LOC
Point Name: LI.AH03.RAD420.LOC
Point Type: LAO
Descriptor: STPT ADJUST
Value: 69.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.RAD460.LOC
Point Name: LI.AH03.RAD460.LOC
Point Type: LAO
Descriptor: STPT ADJUST
Value: 70.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.RAD473.LOC
Point Name: LI.AH03.RAD473.LOC
Point Type: LAO
Descriptor: STPT ADJUST
Value: 65.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV01.OCOC
Point Name: LI.AH03.VAV01.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV01.TMR
Point Name: LI.AH03.VAV01.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 1415.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV02.OCOC
Point Name: LI.AH03.VAV02.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV02.TMR
Point Name: LI.AH03.VAV02.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 6985.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV03.OCOC
Point Name: LI.AH03.VAV03.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV03.TMR
Point Name: LI.AH03.VAV03.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 63125.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV04.OCOC
Point Name: LI.AH03.VAV04.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV04.TMR
Point Name: LI.AH03.VAV04.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 1125.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV05.OCOC
Point Name: LI.AH03.VAV05.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV05.TMR
Point Name: LI.AH03.VAV05.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 6990.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV06.OCOC
Point Name: LI.AH03.VAV06.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV06.TMR
Point Name: LI.AH03.VAV06.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 246870.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV07.OCOC
Point Name: LI.AH03.VAV07.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV07.TMR
Point Name: LI.AH03.VAV07.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 980.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV08.OCOC
Point Name: LI.AH03.VAV08.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV08.TMR
Point Name: LI.AH03.VAV08.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV09.OCOC
Point Name: LI.AH03.VAV09.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV09.TMR
Point Name: LI.AH03.VAV09.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV10.OCOC
Point Name: LI.AH03.VAV10.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV10.TMR
Point Name: LI.AH03.VAV10.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV11.OCOC
Point Name: LI.AH03.VAV11.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV11.TMR
Point Name: LI.AH03.VAV11.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV12.OCOC
Point Name: LI.AH03.VAV12.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV12.TMR
Point Name: LI.AH03.VAV12.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV13.OCOC
Point Name: LI.AH03.VAV13.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV13.TMR
Point Name: LI.AH03.VAV13.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV14.OCOC
Point Name: LI.AH03.VAV14.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV14.TMR
Point Name: LI.AH03.VAV14.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 3960.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV15.OCOC
Point Name: LI.AH03.VAV15.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV15.TMR
Point Name: LI.AH03.VAV15.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 2545.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.AH03.VAV16.OCOC
Point Name: LI.AH03.VAV16.OCOC
Point Type: LDO
Descriptor: OCC OCC
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.AH03.VAV16.TMR
Point Name: LI.AH03.VAV16.TMR
Point Type: LAO
Descriptor: OCC TIMER
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SEC
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.COMMON.AREA.OCC
Point Name: LI.COMMON.AREA.OCC
Point Type: LDO
Descriptor: COMMON OCC PT
Value: DAY
Condition: -N-
Priority: NONE
Text Table: DAY_NIGHT
0 - DAY
1 - NIGHT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.HWDPS
Point Name: LI.HWDPS
Point Type: LAO
Descriptor: HW DIFF PRS STPT
Value: 12.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSID
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.HWENA
Point Name: LI.HWENA
Point Type: LDO
Descriptor: HW SYSTEM ENABLE
Value: ON
Condition: -N-
Priority: OPER
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LI.HWP1.SS
Point Name: LI.HWP1.SS
Point Type: L2SL
Descriptor: HW PUMP 1 SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY2
On/Off Point Address: 1 01 24
Inverted: No
Proof Point Address: 1 01 23
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: LI.HWP1.SVF
Point Name: LI.HWP1.SVF
Point Type: LAO
Descriptor: HWP1 FREQ REF
Value: 63.36
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 1 01 53
Actuator Type L-Type
Slope: 0.006104
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.HWP2.SS
Point Name: LI.HWP2.SS
Point Type: L2SL
Descriptor: HW PUMP 2 SS
Value: OFF
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY2
On/Off Point Address: 1 02 24
Inverted: No
Proof Point Address: 1 02 23
Normally Closed: No
Proof Delay: 60 Informational Text
********************************************************************************
Point System Name: LI.HWP2.SVF
Point Name: LI.HWP2.SVF
Point Type: LAO
Descriptor: HWP2 FREQ REF
Value: 63.39
Condition: -N-
Priority: OVRD
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 1 02 53
Actuator Type L-Type
Slope: 0.006104
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.HWVD
Point Name: LI.HWVD
Point Type: LAO
Descriptor: HWP FREQ REF
Value: 63.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PERCNT
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LI.PNL01.SHEDTMR
Point Name: LI.PNL01.SHEDTMR
Point Type: LAO
Descriptor: MBC01 SHED TIMER
Value: 61232304.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: SECS
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA.MBC.HTG
Point Name: LIA.MBC.HTG
Point Type: LDO
Descriptor: HTG LOCKOUT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA.MBC17.OAT
Point Name: LIA.MBC17.OAT
Point Type: LAO
Descriptor: VIRT OAT
Value: 60.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1.MAX.DMPR.COMD
Point Name: LIA1.MAX.DMPR.COMD
Point Type: LAO
Descriptor:
Value: 97.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: %
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1CV
Point Name: LIA1CV
Point Type: LAO
Descriptor: COOLING VALVE
Value: 14.48
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 01
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA1DA
Point Name: LIA1DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 55.68
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 05 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA1DC
Point Name: LIA1DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA1DS
Point Name: LIA1DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1HV
Point Name: LIA1HV
Point Type: LAO
Descriptor: HUMID VALVE
Value: 4.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 05
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA1IV
Point Name: LIA1IV
Point Type: LAO
Descriptor: VANE CONTROL
Value: 14.49
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 01
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA1LO
Point Name: LIA1LO
Point Type: LAO
Descriptor:
Value: 50.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1MS
Point Name: LIA1MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 47.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1MT
Point Name: LIA1MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 71.7
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 120.0
Low Limit: 40.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -28.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA1NC
Point Name: LIA1NC
Point Type: LDO
Descriptor: NIGHT COOLING
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA1OC
Point Name: LIA1OC
Point Type: LDO
Descriptor: AHU1 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA1PS
Point Name: LIA1PS
Point Type: LAO
Descriptor: PRESS SETPNT
Value: 0.86
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.05
********************************************************************************
Point System Name: LIA1R
Point Name: LIA1R
Point Type: LAO
Descriptor:
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1RH
Point Name: LIA1RH
Point Type: LAI
Descriptor: RET AIR HUMD
Value: 80.69
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1RS
Point Name: LIA1RS
Point Type: L2SL
Descriptor: AHU 3 RETURN SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: LIBRARY2
On/Off Point Address: 2 02 24
Inverted: No
Proof Point Address: 2 02 23
Normally Closed: No
Proof Delay: 240 Informational Text
********************************************************************************
Point System Name: LIA1SH
Point Name: LIA1SH
Point Type: LAO
Descriptor: HUMID SETPNT
Value: 35.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA1SP
Point Name: LIA1SP
Point Type: LAI
Descriptor: DUCT PRESS
Value: 0.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000406
Intercept: -7.5
COV Limit: 0.09984
********************************************************************************
Point System Name: LIA1SS
Point Name: LIA1SS
Point Type: L2SL
Descriptor: AHU 1 SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: LIBRARY2
On/Off Point Address: 2 01 24
Inverted: No
Proof Point Address: 2 01 23
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: LIA1SSS
Point Name: LIA1SSS
Point Type: LDO
Descriptor:
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 08 04
Inverted: No
********************************************************************************
Point System Name: LIA1ST
Point Name: LIA1ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 70.76
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 80.0
Low Limit: 55.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -7.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA1SV
Point Name: LIA1SV
Point Type: LAO
Descriptor: HEATING VALVE
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 06
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA1WA
Point Name: LIA1WA
Point Type: LDI
Descriptor: WATER ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 03 01
Normally Closed: No
********************************************************************************
Point System Name: LIA2.MAX.DMPR.COMD
Point Name: LIA2.MAX.DMPR.COMD
Point Type: LAO
Descriptor:
Value: 75.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: %
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA2CV
Point Name: LIA2CV
Point Type: LAO
Descriptor: COOLING VALVE
Value: 9.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 02
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA2DA
Point Name: LIA2DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 52.57
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 09 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA2DC
Point Name: LIA2DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA2DS
Point Name: LIA2DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA2HV
Point Name: LIA2HV
Point Type: LAO
Descriptor: HUMID VALVE
Value: 4.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 07
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA2LO
Point Name: LIA2LO
Point Type: LAO
Descriptor:
Value: 50.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA2MS
Point Name: LIA2MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 47.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA2MT
Point Name: LIA2MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 75.28
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 120.0
Low Limit: 45.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA2NC
Point Name: LIA2NC
Point Type: LDO
Descriptor: NIGHT COOLING
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA2OC
Point Name: LIA2OC
Point Type: LDO
Descriptor: AHU2 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA2PS
Point Name: LIA2PS
Point Type: LAO
Descriptor: PRESS SETPNT
Value: 0.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.05
********************************************************************************
Point System Name: LIA2R
Point Name: LIA2R
Point Type: LAO
Descriptor:
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA2RH
Point Name: LIA2RH
Point Type: LAI
Descriptor: RET AIR HUMD
Value: 35.1
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -21.00014
COV Limit: 1.0
********************************************************************************
Point System Name: LIA2RS
Point Name: LIA2RS
Point Type: L2SL
Descriptor: AHU 2 RETURN SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: LIBRARY2
On/Off Point Address: 2 04 24
Inverted: No
Proof Point Address: 2 04 23
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: LIA2SH
Point Name: LIA2SH
Point Type: LAO
Descriptor: HUMID SETPNT
Value: 35.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA2SP
Point Name: LIA2SP
Point Type: LAI
Descriptor: DUCT PRESS
Value: 0.32
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.24996
COV Limit: 0.09984
********************************************************************************
Point System Name: LIA2SS
Point Name: LIA2SS
Point Type: L2SL
Descriptor: AHU 2 SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: LIBRARY2
On/Off Point Address: 2 03 24
Inverted: No
Proof Point Address: 2 03 23
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: LIA2ST
Point Name: LIA2ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 70.39
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 80.0
Low Limit: 55.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -6.4993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA2SV
Point Name: LIA2SV
Point Type: LAO
Descriptor: STEAM VALVE
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 02 02
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA2WA
Point Name: LIA2WA
Point Type: LDI
Descriptor: WATER ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 03 02
Normally Closed: No
********************************************************************************
Point System Name: LIA3.MAX.DMPR.COMD
Point Name: LIA3.MAX.DMPR.COMD
Point Type: LAO
Descriptor:
Value: 100.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: %
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA3CV
Point Name: LIA3CV
Point Type: LAO
Descriptor: cooling valve
Value: 9.92
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 03
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA3DA
Point Name: LIA3DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 54.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 09 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA3DC
Point Name: LIA3DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA3DS
Point Name: LIA3DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA3HV
Point Name: LIA3HV
Point Type: LAO
Descriptor: HUMID VALVE
Value: 11.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 06
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA3LO
Point Name: LIA3LO
Point Type: LAO
Descriptor:
Value: 50.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA3MS
Point Name: LIA3MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 47.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA3MT
Point Name: LIA3MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 67.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 120.0
Low Limit: 45.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA3NC
Point Name: LIA3NC
Point Type: LDO
Descriptor: NIGHT COOLING
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA3OC
Point Name: LIA3OC
Point Type: LDO
Descriptor: AHU3 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA3PS
Point Name: LIA3PS
Point Type: LAO
Descriptor: PRESS SETPNT
Value: 1.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.05
********************************************************************************
Point System Name: LIA3R
Point Name: LIA3R
Point Type: LAO
Descriptor:
Value: 74.05
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA3RH
Point Name: LIA3RH
Point Type: LAI
Descriptor: RET AIR HUMD
Value: 25.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 02 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA3RS
Point Name: LIA3RS
Point Type: L2SL
Descriptor: AHU 3 RETURN SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: LIBRARY2
On/Off Point Address: 2 07 24
Inverted: No
Proof Point Address: 2 07 23
Normally Closed: No
Proof Delay: 240 Informational Text
********************************************************************************
Point System Name: LIA3SH
Point Name: LIA3SH
Point Type: LAO
Descriptor: HUMID SETPNT
Value: 35.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA3SP
Point Name: LIA3SP
Point Type: LAI
Descriptor: DUCT PRESS
Value: 1.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 02 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000406
Intercept: -7.5
COV Limit: 0.09984
********************************************************************************
Point System Name: LIA3SS
Point Name: LIA3SS
Point Type: L2SL
Descriptor: AHU 3 SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: LIBRARY2
On/Off Point Address: 2 05 24
Inverted: No
Proof Point Address: 2 05 23
Normally Closed: No
Proof Delay: 240 Informational Text
********************************************************************************
Point System Name: LIA3ST
Point Name: LIA3ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 67.23
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 80.0
Low Limit: 55.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -5.4993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA3SV
Point Name: LIA3SV
Point Type: LAO
Descriptor: HEATING VALVE
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 02 03
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA3WA
Point Name: LIA3WA
Point Type: LDI
Descriptor: WATER ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 03 03
Normally Closed: No
********************************************************************************
Point System Name: LIA4CV
Point Name: LIA4CV
Point Type: LAO
Descriptor: COOLING VALVE
Value: 9.74
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA4DA
Point Name: LIA4DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 55.14
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 09 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA4DC
Point Name: LIA4DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 10.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA4DS
Point Name: LIA4DS
Point Type: LAO
Descriptor: DIS AIR STPT
Value: 55.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA4HV
Point Name: LIA4HV
Point Type: LAO
Descriptor: HUMID VALVE
Value: 4.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 03 08
Actuator Type Voltage
Slope: 0.000655
Intercept: 0.0
COV Limit: 0.994
********************************************************************************
Point System Name: LIA4LO
Point Name: LIA4LO
Point Type: LAO
Descriptor:
Value: 50.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA4MS
Point Name: LIA4MS
Point Type: LAO
Descriptor: MIX AIR STPT
Value: 47.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA4MT
Point Name: LIA4MT
Point Type: LAI
Descriptor: MIX AIR TEMP
Value: 64.52
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 08
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA4NC
Point Name: LIA4NC
Point Type: LDO
Descriptor: NIGHT COOLING
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA4OC
Point Name: LIA4OC
Point Type: LDO
Descriptor: AHU4 OCCUPY
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIA4PS
Point Name: LIA4PS
Point Type: LAO
Descriptor: PRESS SETPNT
Value: 1.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA4R
Point Name: LIA4R
Point Type: LAO
Descriptor:
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA4RH
Point Name: LIA4RH
Point Type: LAI
Descriptor: RET AIR HUMD
Value: 40.6
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 02 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -18.00014
COV Limit: 1.0
********************************************************************************
Point System Name: LIA4SH
Point Name: LIA4SH
Point Type: LAO
Descriptor: HUMID SETPNT
Value: 35.0
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA4SP
Point Name: LIA4SP
Point Type: LAI
Descriptor: DUCT PRESS
Value: 0.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: INCHES
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 02 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.000203
Intercept: -1.25
COV Limit: 0.09984
********************************************************************************
Point System Name: LIA4SS
Point Name: LIA4SS
Point Type: L2SL
Descriptor: AHU 4 SS
Value: ON
Condition: -N-
Priority: OVRD
Text Table: Default L2SL
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: Hours
Field Panel: LIBRARY2
On/Off Point Address: 2 06 24
Inverted: No
Proof Point Address: 2 06 23
Normally Closed: No
Proof Delay: 120 Informational Text
********************************************************************************
Point System Name: LIA4ST
Point Name: LIA4ST
Point Type: LAI
Descriptor: SPACE TEMP
Value: 71.98
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 80.0
Low Limit: 55.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 05 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.4993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA4SV
Point Name: LIA4SV
Point Type: LAO
Descriptor: STEAM VALVE
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 02 04
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA4XX
Point Name: LIA4XX
Point Type: LAO
Descriptor:
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA5CV
Point Name: LIA5CV
Point Type: LAO
Descriptor: COOLING CNTRL
Value: 16.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 02 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.5
********************************************************************************
Point System Name: LIA5DA
Point Name: LIA5DA
Point Type: LAI
Descriptor: DIS AIR TEMP
Value: 59.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 125.0
Low Limit: 40.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 05 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA5DC
Point Name: LIA5DC
Point Type: LAO
Descriptor: MIX AIR DMPR
Value: 15.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 07
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA5HC
Point Name: LIA5HC
Point Type: LAO
Descriptor: HEATING CNTRL
Value: 8.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 08
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA5HS
Point Name: LIA5HS
Point Type: LAO
Descriptor: HUMID SETPNT
Value: 35.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA5HV
Point Name: LIA5HV
Point Type: LAO
Descriptor: HUMID VALVE
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 02 01
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIA5R
Point Name: LIA5R
Point Type: LAO
Descriptor: LOOP
Value: 45.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units:
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA5RS
Point Name: LIA5RS
Point Type: LAO
Descriptor: ROOM SETPNT
Value: 60.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 70.0
Low Limit: 55.0
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIA5SS
Point Name: LIA5SS
Point Type: LDI
Descriptor: AHU5 ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 03 05
Normally Closed: Yes
********************************************************************************
Point System Name: LIARWA
Point Name: LIARWA
Point Type: LDI
Descriptor: ARCHIVE ALM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 03 07
Normally Closed: Yes
********************************************************************************
Point System Name: LIBLDP
Point Name: LIBLDP
Point Type: LAI
Descriptor: BLDG PRESS
Value: 0.02
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 02 06
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.00002
Intercept: -0.37491
COV Limit: 0.1
********************************************************************************
Point System Name: LIBLDS
Point Name: LIBLDS
Point Type: LAO
Descriptor: BLDG PPRESS STPT
Value: 0.01
Condition: -N-
Priority: OPER
Analog Representation: Float
# of decimal places: 2
Engineering Units: IN H2O
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 0.01
********************************************************************************
Point System Name: LIBRARY.ELEC
Point Name: LIBRARY.ELEC
Point Type: LPACI
Descriptor: LPACI
Value: 6512676.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 04
Gain: 1.0
Count Both Edges: No
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.ELEC.DEMAND
Point Name: LIBRARY.ELEC.DEMAND
Point Type: LAO
Descriptor: ELECTRIC DEMAND
Value: 95.25
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KWH
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.ELEC.METER.READING
Point Name: LIBRARY.ELEC.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 6512676.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: LIBRARY.H2O.METER.READING
Point Name: LIBRARY.H2O.METER.READING
Point Type: LAO
Descriptor: TOTAL CONSUMPTN
Value: 14083871
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 10.0
********************************************************************************
Point System Name: LIBRARY.LAST.MONTH.ELEC.CONSUM
Point Name: LIBRARY.LAST.MONTH.ELEC.CONSUM
Point Type: LAO
Descriptor: LAST MNTH CONSMP
Value: 53290.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.LAST.MONTH.H2O.CONSUMP
Point Name: LIBRARY.LAST.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST MNTH CONSMP
Value: 43690
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.LAST.MONTH.STEAM.CONSU
Point Name: LIBRARY.LAST.MONTH.STEAM.CONSU
Point Type: LAO
Descriptor: LAST MONTH STEAM
Value: 8179.17
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: LIBRARY.LAST.WEEK.ELEC.CONSUMP
Point Name: LIBRARY.LAST.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 12948.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.LAST.WEEK.H2O.CONSUMP
Point Name: LIBRARY.LAST.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: LAST WEEK CONSMP
Value: 14500
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.LAST.WEEK.STEAM.CONSU
Point Name: LIBRARY.LAST.WEEK.STEAM.CONSU
Point Type: LAO
Descriptor: LAST WEEK STEAM
Value: 1331.96
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: LIBRARY.MONTH.ELEC.CONSUMP
Point Name: LIBRARY.MONTH.ELEC.CONSUMP
Point Type: LAO
Descriptor: THIS MNTH CONSMP
Value: 28173.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.MONTH.H2O.CONSUMP
Point Name: LIBRARY.MONTH.H2O.CONSUMP
Point Type: LAO
Descriptor: THIS MNTH CONSMP
Value: 33940
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.MONTH.STEAM.CONSUMP
Point Name: LIBRARY.MONTH.STEAM.CONSUMP
Point Type: LAO
Descriptor: MONTH STEAM
Value: 2612.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: LIBRARY.STEAM.DEMAND
Point Name: LIBRARY.STEAM.DEMAND
Point Type: LAI
Descriptor: STEAM DEMAND
Value: 4.13
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM/HR
Alarm Type: Not Alarmable
Totalization: Hours
Field Panel: LIBRARY2
Point Address: 0 02 07
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.336385
Intercept: -2066.75
COV Limit: 50.0
********************************************************************************
Point System Name: LIBRARY.TODAY.ELEC.CONSUMP
Point Name: LIBRARY.TODAY.ELEC.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 1080.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.TODAY.H2O.CONSUMP
Point Name: LIBRARY.TODAY.H2O.CONSUMP
Point Type: LAO
Descriptor: TODAY CONSUMPT
Value: 1120
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.TODAY.STEAM.CONSUMP
Point Name: LIBRARY.TODAY.STEAM.CONSUMP
Point Type: LAO
Descriptor: TODAY STEAM
Value: 53.34
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: LIBRARY.TUNNEL
Point Name: LIBRARY.TUNNEL
Point Type: LDI
Descriptor: DOOR ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LEIGHTON
Point Address: 0 09 10
Normally Closed: Yes
********************************************************************************
Point System Name: LIBRARY.WATER.DEMAND
Point Name: LIBRARY.WATER.DEMAND
Point Type: LAO
Descriptor: H2O DEMAND
Value: 247.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.WATER.HI
Point Name: LIBRARY.WATER.HI
Point Type: LPACI
Descriptor: LPACI
Value: 14008340.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 02
Gain: 10.0
Count Both Edges: No
COV Limit: 10.0
********************************************************************************
Point System Name: LIBRARY.WATER.HIGH
Point Name: LIBRARY.WATER.HIGH
Point Type: LAO
Descriptor: PDL WATER HIGH
Value: 247.5
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.WATER.LO
Point Name: LIBRARY.WATER.LO
Point Type: LPACI
Descriptor: LPACI
Value: 75531.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 03
Gain: 1.0
Count Both Edges: No
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.WATER.LOW
Point Name: LIBRARY.WATER.LOW
Point Type: LAO
Descriptor: PDL WATER LOW
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: GPM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.WEEK.ELEC.CONSUMP
Point Name: LIBRARY.WEEK.ELEC.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.WEEK.H2O.CONSUMP
Point Name: LIBRARY.WEEK.H2O.CONSUMP
Point Type: LAO
Descriptor: WEEK CONSUMPT
Value: 0
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.WEEK.STEAM.CONSUMP
Point Name: LIBRARY.WEEK.STEAM.CONSUMP
Point Type: LAO
Descriptor: WEEK STEAM
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: LIBRARY.YEST.ELEC.CONSUMP
Point Name: LIBRARY.YEST.ELEC.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 1587.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: KW
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.YEST.H2O.CONSUMP
Point Name: LIBRARY.YEST.H2O.CONSUMP
Point Type: LAO
Descriptor: YEST CONSUMPT
Value: 1140
Condition: -N-
Priority: NONE
Analog Representation: Integer
# of decimal places: 2
Engineering Units: GAL
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIBRARY.YEST.STEAM.CONSUMP
Point Name: LIBRARY.YEST.STEAM.CONSUMP
Point Type: LAO
Descriptor: YEST STEAM
Value: 121.91
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: LBM
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 100.0
********************************************************************************
Point System Name: LICHWR
Point Name: LICHWR
Point Type: LAI
Descriptor: CHW RET TEMP
Value: 53.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 05 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
Point System Name: LICHWS
Point Name: LICHWS
Point Type: LAI
Descriptor: CHW SUP TEMP
Value: 47.11
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 05 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.007324
Intercept: -13.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LICONM
Point Name: LICONM
Point Type: LPACI
Descriptor: LIBRARY CND MTR
Value: 0.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 4
Engineering Units: GAL
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 04 01
Gain: 1.0
Count Both Edges: No
COV Limit: 1.0
********************************************************************************
Point System Name: LICONS
Point Name: LICONS
Point Type: LAO
Descriptor: CONV SETPNT
Value: 126.99
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LICORP
Point Name: LICORP
Point Type: LDO
Descriptor: CONDEN RPT
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIDEWF
Point Name: LIDEWF
Point Type: LAI
Descriptor: OA DEWPOINT
Value: 26.24
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 09 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.006918
Intercept: -83.80106
COV Limit: 1.00279
********************************************************************************
Point System Name: LIECON
Point Name: LIECON
Point Type: LDO
Descriptor: ECONOMIZE MD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIEMTS
Point Name: LIEMTS
Point Type: LDI
Descriptor: LI EMER TS
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 03 04
Normally Closed: No
********************************************************************************
Point System Name: LIEXF1
Point Name: LIEXF1
Point Type: LDO
Descriptor: EX FAN 1SS
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 08 05
Inverted: No
********************************************************************************
Point System Name: LIEXF4
Point Name: LIEXF4
Point Type: L2SL
Descriptor: LIB 4TH FLR EXF
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default L2SL
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY2
On/Off Point Address: 0 04 01
Inverted: No
Proof Point Address: 0 05 01
Normally Closed: No
Proof Delay: 30 Informational Text
********************************************************************************
Point System Name: LIFIRE
Point Name: LIFIRE
Point Type: LDI
Descriptor: FIRE ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 01 01
Normally Closed: No
********************************************************************************
Point System Name: LIFREECOOL
Point Name: LIFREECOOL
Point Type: LDO
Descriptor: FREE.COOL
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIHUMD
Point Name: LIHUMD
Point Type: LAO
Descriptor: HUMIDITY
Value: 62.4
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PCNTRH
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 2.0
********************************************************************************
Point System Name: LIHWCV
Point Name: LIHWCV
Point Type: LAO
Descriptor: HW CONV VLVE
Value: 7.01
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 01 05
Actuator Type Voltage
Slope: 0.000651
Intercept: 0.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIHWDP
Point Name: LIHWDP
Point Type: LAI
Descriptor: HW DIF PRESS
Value: 11.94
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PSI
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY2
Point Address: 0 02 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.001017
Intercept: -6.25011
COV Limit: 0.2
********************************************************************************
Point System Name: LIHWLD
Point Name: LIHWLD
Point Type: LDO
Descriptor: HW PMP LEAD
Value: ON
Condition: -N-
Priority: NONE
Text Table: Default LDO
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
********************************************************************************
Point System Name: LIHWRT
Point Name: LIHWRT
Point Type: LAI
Descriptor: HW RET TEMP
Value: 116.54
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 199.99
Low Limit: 49.99
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 05 04
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.006103
Intercept: 32.50106
COV Limit: 1.00189
********************************************************************************
Point System Name: LIHWST
Point Name: LIHWST
Point Type: LAI
Descriptor: HW SUP TEMP
Value: 127.09
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 210.0
Low Limit: 65.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 05 05
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.006103
Intercept: 32.50106
COV Limit: 1.00189
********************************************************************************
Point System Name: LISWGA
Point Name: LISWGA
Point Type: LDI
Descriptor: SEWAGE ALARM
Value: OFF
Condition: -N-
Priority: NONE
Text Table: Default LDI
0 - OFF
1 - ON
Access Group(s): <all>
Alarm Type: Standard Alarms
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 03 06
Normally Closed: No
********************************************************************************
Point System Name: LITEMP
Point Name: LITEMP
Point Type: LAI
Descriptor: LIBERARY OAT
Value: 66.38
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 10 03
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.007324
Intercept: -103.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV01.ORGSTPT
Point Name: LIV01.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV02.ORGSTPT
Point Name: LIV02.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV04.ORGSTPT
Point Name: LIV04.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV05.ORGSTPT
Point Name: LIV05.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV07.ORGSTPT
Point Name: LIV07.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV09.ORGSTPT
Point Name: LIV09.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV10.ORGSTPT
Point Name: LIV10.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV14.ORGSTPT
Point Name: LIV14.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV16.ORGSTPT
Point Name: LIV16.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV18.ORGSTPT
Point Name: LIV18.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV21.ORGSTPT
Point Name: LIV21.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV23.ORGSTPT
Point Name: LIV23.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV24.ORGSTPT
Point Name: LIV24.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV25.ORGSTPT
Point Name: LIV25.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV26.ORGSTPT
Point Name: LIV26.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV29.ORGSTPT
Point Name: LIV29.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV30.ORGSTPT
Point Name: LIV30.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV33.ORGSTPT
Point Name: LIV33.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV34.ORGSTPT
Point Name: LIV34.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV36.ORGSTPT
Point Name: LIV36.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV37.ORGSTPT
Point Name: LIV37.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 74.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV38.ORGSTPT
Point Name: LIV38.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV39.ORGSTPT
Point Name: LIV39.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV41.ORGSTPT
Point Name: LIV41.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV42.ORGSTPT
Point Name: LIV42.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV45.ORGSTPT
Point Name: LIV45.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV47.ORGSTPT
Point Name: LIV47.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV49.ORGSTPT
Point Name: LIV49.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV51.ORGSTPT
Point Name: LIV51.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV54.ORGSTPT
Point Name: LIV54.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV55.ORGSTPT
Point Name: LIV55.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV60.ORGSTPT
Point Name: LIV60.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV61.ORGSTPT
Point Name: LIV61.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV62.ORGSTPT
Point Name: LIV62.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV63.ORGSTPT
Point Name: LIV63.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV64.ORGSTPT
Point Name: LIV64.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV65.ORGSTPT
Point Name: LIV65.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV66.ORGSTPT
Point Name: LIV66.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV67.ORGSTPT
Point Name: LIV67.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV68.ORGSTPT
Point Name: LIV68.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV71.ORGSTPT
Point Name: LIV71.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV72.ORGSTPT
Point Name: LIV72.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV75.ORGSTPT
Point Name: LIV75.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV76.ORGSTPT
Point Name: LIV76.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV77.ORGSTPT
Point Name: LIV77.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIV80.ORGSTPT
Point Name: LIV80.ORGSTPT
Point Type: LAO
Descriptor: ORIG CTL STPT
Value: 72.0
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Alarm Type: Not Alarmable
Totalization: None
Field Panel: LIBRARY1
Point Address: -Virtual-
Actuator Type Voltage
Slope: 1.0
Intercept: 0.0
COV Limit: 1.0
********************************************************************************
Point System Name: LIVALH
Point Name: LIVALH
Point Type: LAI
Descriptor: VAULT HUMID
Value: 41.72
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: PER RH
Alarm Type: Standard Alarms
High Limit: 50.0
Low Limit: 30.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 09 01
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -25.0
COV Limit: 0.99994
********************************************************************************
Point System Name: LIVALT
Point Name: LIVALT
Point Type: LAI
Descriptor: VAULT TEMP
Value: 64.2
Condition: -N-
Priority: NONE
Analog Representation: Float
# of decimal places: 2
Engineering Units: DEG F
Access Group(s): <all>
Alarm Type: Standard Alarms
High Limit: 75.0
Low Limit: 50.0
Totalization: None
Field Panel: LIBRARY1
Point Address: 0 09 02
Sensor Type: Current
Wire Resistance: 0.0
Slope: 0.004069
Intercept: -4.9993
COV Limit: 0.99994
********************************************************************************
******************************** End of Report *********************************