## Sheet1
Energy Management Team: Issue Tracking Log
Buildings: | Graph type(s): | Date reviewed | Comments: | Resolution: | Status: | Date complete:
Willis | Load profile analysis | 2017-05-03 | high electric load during the week - AC?; strong cyclical activity. Is fan turning on and off based on maintaining set back temperatures relative to outside air. |  | resolved | 2017-05-03
Leighton | Load profile anlaysis | 2017-05-03 | spikes at 8pm on Sundays. looks like there are three stages (three fans). One fan looks like it's running all night long. Fan is running to maintain set point relative to outside temperature. |  | resolved | 2017-05-03
Boliou | Load profile anlaysis | 2016-09-29 | heating and electric operating simulataneously?; high activity at night; building never goes to bed; lights stay on in the sculpture studio |  | unresolved
LDC | Load profile anlaysis | 2017-06-02 | compare base load to peak load profile analyses for before and after LDC kitchen hood project- Do trend analysis last full week of school fall term. First full week after thanksgiving. Last week in January. Spring Break. Load profile for the last 12 months. look at condesate and electricity. |  | unresolved
LDC | Trend analysis | 2017-06-02 | Analysis of Kitchen Hood Project, it doesn't look like it's changing that much. Peaks (37 kWh) and troughs (10kWh) are about the same throughout the 2016-2017 academic school year. We need to focus on the minutes between the peaks. |  | unresolved
LDC | Heat Map | 2017-06-02 | Green edges really tighted up after the Kitchen Hood project was implemented. It went from light green/yellow to dark green during the night times after project installation in November. |  | unresolved
LDC | Project Measurement and Verification | 2017-06-02 | It seems to be only saving about $500 a month. This may be because a lot of the data in April was missing. This could also be because LDC workers are shutting off the sensors. |  | unresolved
Laird Stadium | Load profile anlaysis | 2016-10-25 | Laird Stadium had a high base load 9/22-9/29 | Flood? | resolved
Laird Hall | Load profile anlaysis | 2016-11-08 | energy oscillations | telecomm air conditiong load turning on and off? | unresolved
Cowling | Heat map anlaysis | 2016-10-25 | high electricity use from 12:00am-6:00am |  | unresolved
West Gym | Heat map anlaysis | 2016-10-25 | high load during 12/18-12/20 | painting project and Lighten Up | resolved
Goodhue | Load profile analysis |  |  |  | resolved | 2017-05-03
CMC | Load profile analysis |  | weird dip in activity is a meter problem; output goes from 120 KW to 180 KW during the weekday | CMC has a high energy load | resolved | 2017-05-03
Gould Library | Load profile analysis |  | schedules are working as designed |  | resolved | 2017-05-03
Rec Center | Trend analysis | 2017-05-17 | high base load (60kW) and high peak load (100kW), similar to CMC; drops approx. 20kW during breaks |  | unresolved
Cowling | Heat map anlaysis | 2017-05-17 | significant drop in energy use during winter break--is this related to lighting or mechanical equipment? |  | unresolved
Weitz | Heat map anlaysis | 2017-05-24 | electricity use during the day is notably greater during Jan and Feb compared to March and April |  | unresolved
Mudd Hall | Trend analysis |  | Energy use doesn't decrease significantly during spring break compared to winter term - look at winter break |  | unresolved
Watson Hall | Load Profile analysis | 2017-06-02 | Great! Good comparison to Myers and Nourse. What are we doing differently in Watson? |  | unresolved
Myers Hall | Load Profile analysis | 2017-06-02 | Weird variation in the day. Does not shut down enough at night compared to Watson even though they have about the same occupancy. |  | unresolved
Nourse Hall | Load Profile analysis | 2017-06-02 | Weird variation in the day. Does not shut down enough at night compared to Watson even though they have about the same occupancy. |  | unresolved
Watson Hall | Heat map analysis | 2017-06-02 | Great heat map! Why is Watson so much tighter and greener at night compared to Myers and Nourse? Vertical building, better air circulation? |  | unresolved
Myers Hall | Heat map analysis | 2017-06-02 | Great heat map! Why is Watson so much tighter and greener at night compared to Myers and Nourse? Not a veritical building, students maybe use a lot of fans? |  | unresolved
Nourse Hall | Heat map analysis | 2017-06-02 | Great heat map! Why is Watson so much tighter and greener at night compared to Myers and Nourse? Not a veritical building, students maybe use a lot of fans? |  | unresolved
Davis | Heat map analysis | 1/1/17-3/20/17 | Great heat map! Why is electricity use so high during winter term 2017? Heating is from steam, so we don't expect so much electricity use. Anamoly starts and ends along with winter term. |  | unresolved
Severance | Heat map analysis |  | Martha wants to do a meter audit. Heat map is kind of weird! General patterns are obscured by apparent building usage. |  | unresolved
Burton Hall | Heat map analysis |  | No issues |  | Closed