## Energy Audits
Carleton College Energy Conservation Program
Building Energy Audits Detail
|  | Auditor | Audit Cost | Est. Rebate | Actual Rebate | Audit Net Cost | ECMs Recommended | ECMs Pursuing | ECM Cost | Est. Rebates | ECM Savings | Payback | Elec savings (kWh) | Gas savings (Dth) | Water savings (kgal) | Notes
FY2012
| Residential Houses (10) | NEC | 3500 | N/A | 0 | 3500 | Multiple
| Subtotal - FY2012 |  | 3500 |  | 0 | 3500
FY2013: Athletics
| Laird Stadium | DLR Group | 16000 | 3458 | 138.67 | 15861.33 | 21 | 14 | 28650 | TBD | 4600 | #VALUE! | 38934 | 239.6 | 0 | Not pursuing ECM 5, 14, 15
| Cowling Rec Center | QSE | 24000 | 1475 | 1475 | 22525 | 24 | 20 | 60075 | 14309 | 19102 | 2.3959 | 54423 | 2407 | 0
| West Gym | Sebesta | 24000 | 3000 | 3000 | 21000 | 33 | 18 | 593610 | 3718 | 36004 | 16.8246 | 49052 | 4235.2 | 1376 | Includes $100k to add cooling to pool AHU and $345k for solar thermal water heating
| Rec Center | Dunham | 35500 | 4300 | 4309 | 31191 | 14 | 12 | 8500 | 5509 | 7714 | 4.4312 | 72635 | 455 | 0
| Subtotal - FY2013 |  | 99500 | 12233 | 8922.67 | 90577.33 | 92 | 64 | 690835 | 23536 | 67420 |  | 215044 | 7336.8 | 1376
FY2014: Common Spaces + Science Buildings
| Sayles Hill | Sebesta | 17500 | 0 | 0 | 17500
| Library | Sebesta | 17500 | 0 | 0 | 17500
| Language & Dining Center | Sebesta | 17500 | 0 | 0 | 17500
| Mudd Hall | Siemens | 9230 | 1925 |  | 9230 | 16 |  | 20680 |  | 4833 | 4.2789 | 38209 | 195
| Hulings Hall | Siemens | 9629 | 2195 |  | 9629 | 16 |  | 17580 |  | 4850 | 3.6247 | 51209 | 94
| Olin Hall | Siemens | 9230 | 1925 |  | 9230 | 8 |  | 14840 |  | 4295 | 3.4552 | 36072 | 172
| Subtotal - FY2014 |  | 80589 | 6045 | 0 | 80589 | 40 | 0
FY2017: Academic + Admin (select 4-6 from list)
Boliou Memorial Art Bldg.
Center for Mathematics & Computing
Facilities Building/ Steam Plant
Goodsell Observatory
Laird Hall
Leighton Hall
Music Hall
Weitz Center
Willis Memorial Hall
| Subtotal - FY2012 |  | 0 |  | 0 | 0
FY2018: Residence Halls (select 4-6 from list)
Burton Hall
Davis Hall
Cassat Hall
Evans Hall
Goodhue Hall
James Hall
Musser Hall
Myers Hall
Nourse Hall
Severence Hall
Student Townhomes
| Subtotal - FY2012 |  | 0 |  | 0 | 0
FY2019 - FY2020: Remaining Academic, Admin, Res Halls
| Chapel | N/A

## ECM Summary
Fiscal Year Energy Conservation Measure (ECM) Summary
GENERAL |  | COST (5) | [6 empty] | SAVINGS (6)
Year Complete | Number of Projects | Estimated Cost | Capital Project | CAP Funds | SRF Funds | Maint/Facl Funds | Rebates | Total Cost | Elec (kWh) | Gas (Therms) | Total (MMbtu) | Total MTCDE | Elec Rate (per kWh) | Gas Rate (per Mmbtu) | Total $ | ROI
FY 2010 | 1 | 0 | 0 | 0 | 0 | 143250 | -5554 | 137696 | 319377 | 0 | 1089.7143 | 223.5639 | 0.06 | 5.262 | 24896.6968 | 5.5307
FY 2011 (1) | 2 | 0 | 0 | 0 | 0 | 144350 | -12782 | 131568 | 0 | 0 | 0 | 0 | 0.064 | 5.487 | 0
FY 2012 | 4 | 0 | 0 | 46041 | 0 | 94934 | -10546 | 130429 | 155801.84 | 0 | 531.5959 | 109.0613 | 0.076 | 4.673 | 14325.0874 | 9.1049
FY 2013 (2) | 21 | -536 | 1350000 | 36711 | 100 | 45879.3 | -18763 | 63927.3 | 183793.385 | 8430 | 609.7155 | 170.8054 | 0.07 | 4.339 | 15511.0924 | 4.1214
FY 2014 | 69 | 118456.15 | 0 | 0 | 0 | 253627.903 | -12353.4 | 241274.503 | 428608.9808 | 8165.0014 | 1446.6643 | 340.8513 | 0.074 | 5.727 | 40002.1111 | 6.0315
FY 2015 (3) | 11 | 14386 | 800000 | 43844 | 0 | 9995 | 0 | 10839 | 4408.142 | 10817 | 15.0401 | 57.1707 | 0.074 | 5.727 | 412.3371 | 26.2867
Total | 108 | 132306.15 | 2150000 | 126596 | 100 | 692036.203 | -59998.4 | 715733.803 | 1091989.348 | 27412.0014 | 3692.7301 | 901.4526 |  |  | 95147.3249 | 7.5224
PENDING | 129 | 548225 | 0 | 0 | 0 | 58.5 | 0 | 58.5 | 1001207 | 56990 | 3416.1183 | 985.7949 | 0.074 | 5 | 91169.9097 | 6.0132
N/A (4) | 38 | 804796 | 0 | 3220 | 0 | 7791 | -462 | 10549 | 9006 | 12625 | 97.0476 | 69.4292 | 0.074 | 5 | 1151.682 | 698.8005
NOTES:
(1) Need data from Library controls retrofit
(2) Need data for Grounds Shop lighting retrofit, Cowling locker room lighting retrofit, Musser lighting control timers
(3) Need data for all FY 2015 maintenance lighting upgrades; need to update annual blended util. rates
(4) "N/A" = projects that don’t meet payback requirements and/or are not practical to implement for some reason
(5) Initial costs include both maintenance and energy savings components
(6) This spreadsheet does not incorporate limits on how long a project can be included in payback/savings calculations

## ECM Detail
|  | Energy Conservation Measures Tracking Log |  | 26.29% |  | Red Italics = estimate |  |  |  | Yellow highlight = need info from Maintenance, Xcel, etc. | [19 empty] | 1067302.322 | [11 empty] | 27474.0014 | [6 empty] | 37340.0025
|  | Carleton College (Northfield, MN) |  | TOTALS: | [9 empty] | 0 | 0 | 127640 | 0 | 126596 | 100 | 681982.703 | -59998.4 | 705680.303 | [7 empty] | 2092969.322 |  | 152912.1209 | [9 empty] | 68302.0014 |  | 65951.0543 | 62 |  | 334.8 | 7108.0743 | 208535.6648 | 3.384
|  | PROJECT INFO | [11 empty] | EST. COST (RxC Study) |  |  | ACTUAL COST | [5 empty] | ANNUAL ELECTRIC SAVINGS | [12 empty] | ANNUAL GAS SAVINGS | [8 empty] | WATER SAVINGS |  |  | TOTAL SAVINGS |  | Simple Payback | Maint Savings | Notes
Entered in GRITS | ID | Fiscal Year | Project | Work Order No. | Parts / Labor | Category | Lifespan | Status | Date Complete | Building | Location | SF | Auditor | Cost | Xcel Rebate | Net Cost | Capital Project | CAP Funds | SRF Funds | Maint. Funds | Xcel Rebate | Net Cost | Before Qty | After Qty | Before watts | After watts | Before hrs/yr | After hrs/yr | Hours Saved | kWh Saved | Rate $/kwh | Annual Savings ($) | Demand (kW) | Rate $/kW | Demand Savings ($) | Qty | Before btu/yr | After btu/yr | BTU Saved | Efficiency | Lbs of Steam Saved | Therms Saved | Rate $/therm or lb | Annual Savings | kGAL | Rate | Cost ($) | MMBTU | Cost ($) | Years | Y/N
|  | Laird Stadium Audit: DLR Group | [15 empty] | 0 | 0 | 31158.76 | -450 | 30708.76 | [7 empty] | 12968.657 |  | 571.0823 | [9 empty] | 8430 |  | 0 |  |  |  | 26.8615 | 571.0823 | #DIV/0!
| LS-1 | 2013 | ECM 1 (Prereq) Add DDC controls to AHU 2 |  |  | HVAC | 20 | No rebate | 2012-08-31 | Stadium | Mechanical |  | DLR Group | N/A | N/A | N/A |  | 0 | 0 | Capital | 0 | Capital | [26 empty] | 0
| LS-2 | 2013 | ECM 1 Reduce AHU 2 run time |  |  | HVAC | 20 | Complete?? | complete? | Stadium | Attic |  | DLR Group | 3500 | -4781 | -1281 |  | 0 | 0 |  |  | 0 | [7 empty] | 5096 | 0.07 | 356.72 | [9 empty] | 8430 | [6 empty] | 356.72 |  |  | Need DDC to implement reduction from 24/7/365 operation to 13 hrs/day (winter) and 9 hrs / day (summer)
| LS-3 | 2013 | ECM 2 (Prereq) Add DDC controls to AHU 3 |  |  | HVAC | 20 | Complete - no rebate | Spring 2013 | Stadium | Attic |  | DLR Group / Facilities | N/A | N/A | N/A |  | 0 | 0 | 17965 | N/A | 17965 | [26 empty] | 0
| LS-4 | 2013 | ECM 2 Reduce AHU 3 run time |  |  | HVAC | 20 | Complete?? | complete? | Stadium | Attic |  | DLR Group | 3500 | -4781 | -1281 |  | 0 | 0 |  |  | 0 | [26 empty] | 0 |  |  | Need DDC to implement reduction from 24/7/365 operation to 13 hrs/day (winter) and 9 hrs / day (summer)
| LS-5 | 2014 | ECM 4 (Alt) Lable drying room EF switch |  |  | HVAC | 10 | Not done (no rebate for alt?) |  | Stadium | Ground Floor |  | DLR Group / Facilities | N/A | N/A | N/A |  | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0
| LS-6 | 2013 | ECM 6 Add occ. sensors to North and South lobbies | 358433, 358433A | Work Order 358433 in-house labor: $3,552.50 (includes TRC Invoice 0062188-IN for $1337.86) WO 358433A Cedar Lake Invoice 52009: $6965.54 | Lighting | 15 | COMPLETE | 2013-12-27 | Stadium | Ground Floor |  | DLR Group | 500 | -231 | 269 |  | 0 | 0 | 10518.04 |  | 10518.04 | [26 empty] | 0
| LS-7 | 2013 | ECM 7 Reduce ground and 2nd flr public restroom EF run time (based on occ. Sensor) |  |  | HVAC | 20 | Complete?? |  | Stadium | Ground Floor |  | DLR Group | 400 | -189 | 211 |  |  | 0 |  |  | 0 | [26 empty] | 0
| LS-8 | 2013 | ECM 10 Add occ. sensor to men's locker rooms (varsity + public) | 358433, 358433A | See ECM 6 | Lighting | 15 | See ECM 6 | 2013-12-27 | Stadium | Ground Floor |  | DLR Group | 300 | 0 | 300 |  | 0 | 0 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6
| LS-9 | 2013 | ECM 11 Add occ sensor to women's locker room (varsity) | 358433, 358433A | See ECM 6 | Lighting | 15 | See ECM 6 | 2013-12-27 | Stadium | Ground Floor |  | DLR Group | 300 | 0 | 300 |  | 0 | 0 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6 | See ECM 6
| LS-10 | 2014 | Add: occ sensors on public restrooms (ground and 2nd floor) |  |  | Lighting | 15 | [41 empty] | 0
| LS-11 | 2013 | ECM 8-9 Add photo cell to exterior lights (+LED) - back |  |  | Lighting | 5 | Have TRC quote; need invoice | 2012-08-31 | Stadium | Exterior doors |  | DLR Group / Facilities | 500 | 0 | 500 |  | 0 | 0 | 1337.86 | -225 | 1112.86 |  |  | 1371 | 273 | 4381 | 4381 | 0 | 4810.338 | 0.07 | [16 empty] | 16.4129 | 0 | #DIV/0! |  | Replaced fixture with photocell sensored LED fixture
| LS-12 | 2013 | ECM 8-9 Add photo cell to exterior lights (+LED) - sides |  |  | Lighting | 5 | Have TRC quote; need invoice | 2012-08-31 | Stadium | Exterior doors |  | DLR Group / Facilities | 500 | 0 | 500 |  | 0 | 0 | 1337.86 | -225 | 1112.86 |  |  | 924 | 225 | 4381 | 4381 | 0 | 3062.319 | 0.07 | 214.3623 | [15 empty] | 10.4486 | 214.3623 | 5.1915 |  | Replaced fixture with photocell sensored LED fixture
| LS-13 |  | ECM 3 (Prereq) Add DDC controls to AHU 1 |  |  | HVAC | 20 | Is this required to change scheduling? |  | Stadium | Ground Floor |  | DLR Group / Facilities | N/A | N/A | N/A |  | 0 | 0 |  |  | 0 | [26 empty] | 0
| LS-14 |  | ECM 3 Reduce AHU 1 run time |  |  | HVAC | 20 | Did we change the schedule? |  | Stadium | Ground Floor |  | DLR Group | 1800 | -1966 | -166 |  | 0 | 0 |  |  | 0 | [26 empty] | 0 |  |  | DLR ECM = reduction from 11 hrs/day year-round to 11 hrs/day M-F (winter) and 8 hrs / day M-F (summer); 10/09/13 per Mitch Miller - AHU 1 runs 6:00 - 5:00 heat only and is off when weight room AC is on
| LS-15 | N/A | ECM 4 (Prereq) Tie drying room EF into BAS |  |  | HVAC |  | Not Selected | N/A | Stadium | Ground Floor |  | DLR Group | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A | Reduce from 24/7/365 to 13 hrs/day (winter) and 9 hrs/day (summer)
| LS-16 | N/A | ECM 4 Reduce drying room EF |  |  | HVAC |  | Not Selected | N/A | Stadium | Ground Floor |  | DLR Group | 750 | -123 | 627 |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A | Reduce from 24/7/365 to 13 hrs/day (winter) and 9 hrs/day (summer)
| LS-17 | N/A | ECM 5 Reduce OA delivered to Stadium |  |  | HVAC |  | Not Selected | N/A | Stadium | Mechanical |  | DLR Group | 3000 | -3103 |  |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A | Not pursuing - other priorities (10/29/12)
| LS-18 | N/A | ECM 12 Convert AHU 1 SA to single zone VAV system |  |  | HVAC |  | Not Selected | N/A | Stadium | Ground Floor |  | DLR Group | 5750 | 0 | 5750 |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A | Not pursuing - requires entire AHU replacement
| LS-19 | N/A | ECM 13 Confert AHU 2 SA to single zone VAV system |  |  | HVAC |  | Not Selected | N/A | Stadium | Attic |  | DLR Group | 4175 | 0 | 4175 |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A
| LS-20 | N/A | ECM 14 Convert AHU 3 SA to single zone VAV system |  |  | HVAC |  | Not Selected | N/A | Stadium | Attic |  | DLR Group | 4175 | 0 | 4175 |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A
| LS-21 | N/A | ECM 15 Convert steam system to hot water |  |  | HVAC |  | Not Selected | N/A | Stadium | Floors 1-2 |  | DLR Group | 575800 | 0 | 575800 |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A
|  | Cowling Recreation Center Audit: Question & Solutions Engineering | [15 empty] | 0 | 0 | 61551.28 | 0 | 61551.28 | [7 empty] | 68238 |  | 4795.442 | [9 empty] | 2317 |  | 11585 |  |  |  | 232.8304 | 16070.442 | 4.0919
| CRC-1 | 2014 | ECO-01 Reduce exhaust airflow | 373514 | MMC invoice 20428684: $900.82 (split btwn Rec & Cowling) MMC TAB report dated 1/01/14 (Job #20428684) | HVAC | 20 | COMPLETE | 2014-01-20 | Cowling | All |  | Q&S | 2070 | -708 | 1362 |  | 0 | 0 | 900.82 | 0 | 900.82 | [7 empty] | 8536 | 0.07 | 597.52 | 1.13 | [14 empty] | 29.1248 | 597.52 | 1.5076
| CRC-2 | 2014 | ECO-02 AHU-1 (gym) optimization - add VFD | 373513 - mech 373909 - elec | Work order 373513 in-house labor: $117 Parts and labor included in invoices for ECO-03. | HVAC | 15 | COMPLETE | 2014-01-09 | Cowling | Gymnasium |  | Q&S | 8694 | -3045 | 5649 |  | 0 | 0 | Incl. in ECO-03 | 0 | Incl. in ECO-03 | [7 empty] | 17355 | 0.07 | 1214.85 | 2.55 | [5 empty] | 405 |  |  | 405 | 5 | 2025 |  |  |  | 59.2157 | 3239.85 |  |  | RA CO2 Sensor, Supply Fan VFD, Replace OA and RA dampers (low leak, electronically actuated)
| CRC-3 | 2014 | ECO-03 AHU-2 (tennis, dance, conference) optimization, add dampers + VFD | 373512 - mech 373909 - elec | Work order in-house labor 373512: $0 Work order 373513 in-house labor: $117 Siemens Parts Invoice 5443045736: $288.16 Siemens Parts Invoice 5443036999 $288.16 Siemens Parts Invoice 5442935465 $1126.20 Mulcahy Parts Invoice 253059 - VFDs: $1700.77 MMC invoice 204031691 - mech labor + dampers: $4531.35 Cedar Lake invoice 52007 - elec labor: $6857.44 | HVAC | 15 | COMPLETE | 2014-01-20 | Cowling | Office/Conference/Dance/Lobby/ Tennis/Locker Rooms |  | Q&S | 23184 | -1868 | 21316 |  | 0 | 0 | 14909.08 |  | 14909.08 | [7 empty] | 15002 | 0.07 | 1050.14 | [6 empty] | 237 |  |  | 237 | 5 | 1185 |  |  |  | 51.1871 | 2235.14 | 6.6703 |  | Add VAVs + zone control in Tennis, Dance, Conference Room, replace dampers with low leak / electronically actuated
| CRC-4 | 2014 | ECO-04a Occ sensors: Tennis Court | 373521 |  | Lighting | 15 | COMPLETE | 2014-07-03 | Cowling | Tennis Court |  | Q&S | 30800 | -498 | 30302 |  | 0 | 0 | 10290 |  | 10290 | [7 empty] | 18782 | 0.071 | 1333.522 | [15 empty] | 64.0842 | 1333.522 | 7.7164 |  | Savings based on LED fixtures; used TRC kwh saved number and Carleton's blended rate for elec.
| CRC-5 | 2014 | ECO-04b Occ Sensors: Cowling Basketball Gym | 376690 | TRC Invoice J91431A-IN: $3,575 | Lighting | 15 | COMPLETE | 2014-02-21 | Cowling | Basketball gym |  | Q&S | Incl. in ECO4a | Incl. in ECO4a | Incl. in ECO4a |  | 0 | 0 | 3575 |  | 3575 | [25 empty] | 0 | 0 | 0
| CRC-6 | 2014 | ECO-04c Occ Sensors: Cowling Dance Studio (ADD) | 376441 | TRC Invoice J91341A-IN: $1095 | Lighting | 15 | COMPLETE | 2013-02-10 | Cowling | Dance Studio |  | Maintenance | Incl. in ECO4a | Incl. in ECO4a | Incl. in ECO4a |  | 0 | 0 | 1095 |  | 1095 |  |  | 576 | 576 | 2500 | 1250 | 1250 | 720 | 0.07 | 50.4 | [15 empty] | 2.4566 | 50.4 | 21.7262 |  | Used TRC calcs
| CRC-7 | 2014 | ECO-04d Occ Sensors: Cowling Dance Studio (ADD) | 376440 | TRC Invoice J91342A-IN: $3190 | Lighting | 15 | COMPLETE | 2013-02-10 | Cowling | Dance Studio |  | Maintenance | Incl. in ECO4a | Incl. in ECO4a | Incl. in ECO4a |  |  |  | 3190 |  | 3190 |  |  | 3000 | 576 | 2500 | 2500 | 0 | 6060 | 0.07 | 424.2 | [15 empty] | 20.6767 | 424.2 | 7.52 |  | Used TRC calcs
| CRC-8 | 2014 | ECO-06 AHU-3 (pool) steam valve leaking | 401751 | Siemens Parts Invoice 5443045736: $228.68 Work Order in-house labor: $58.50 | HVAC | 10 | COMPLETE | 2014-04-01 | Cowling | Mechanical |  | Q&S | 2760 | -32 | 2728 |  | 0 | 0 | 287.18 |  | 287.18 | [16 empty] | 586 |  |  | 586 | 5 | 2930 |  |  |  | 0.000586 | 2930 | 0.098014 |  | Savings would drop to $233 per year if ECO-07 is implemented
| CRC-9 | 2014 | ECO-08 Reduce setpoint: Tennis Court | 373522 | Work order in-house labor: $29.25 | HVAC | 20 | COMPLETE | 2014-01-09 | Cowling | Lower Level |  | Q&S | 28 | 0 | 28 |  | 0 | 0 | 29.25 |  | 29.25 | [16 empty] | 137 |  |  | 137 | 5 | 685 |  |  |  | 0.000137 | 685 | 0.042701 |  | Assumes AHU-2 optimization is complete; not possible without zoning that unit
| CRC-10 | 2014 | ECO-09 Reduce setpoint: Lobby (set to 68 degrees) | 373523 | Work order in-house labor: $29.25 | HVAC | 20 | COMPLETE | 2014-01-09 | Cowling | Main Level |  | Q&S | 28 | 0 | 28 |  | 0 | 0 | 29.25 |  | 29.25 | [16 empty] | 18 |  |  | 18 | 5 | 90 |  |  |  | 1.8e-05 | 90 | 0.325 |  | Assumes AHU-2 optimization is complete; not possible without zoning that unit
| CRC-11 | 2014 | ECO-10 Clean AHU-1 steam coil | 373524 | Work order in-house labor: $58.50 | HVAC | 5 | COMPLETE | 2014-01-31 | Cowling | Mechanical |  | Q&S | 1104 | 0 | 1104 |  | 0 | 0 | 58.5 |  | 58.5 | [7 empty] | 1783 | 0.07 | 124.81 | [15 empty] | 6.0836 | 124.81 | 0.46871 |  | Savings assume AHU-1 optimization not implemented
| CRC-12 | 2014 | ECO-11 Dance Room reheat valve leaking: replace | 373525 | Work Order 373526 in-house labor: $175.50 Siemens Invoice 5443092714: $308.16 | HVAC | 10 | COMPLETE |  | Cowling | Main Level |  | Q&S | 1380 | -165 | 1215 |  | 0 | 0 | 483.66 |  | 483.66 | [16 empty] | 33 |  |  | 33 | 5 | 165 |  |  |  | 3.3e-05 | 165 | 2.9313 |  | Cost assumes pneumatic actuator, not electronic; savings assume ECO-03 is not completed
| CRC-13 | 2014 | ECO-13 AHU-2 steam valve leaking | 373526 | Work Order 373526 in-house labor: $175.50 Siemens Parts Invoice 5443036999: $288.16 | HVAC | 10 | COMPLETE | 2013-01-09 | Cowling | Mechanical |  | Q&S | 276 | 0 | 276 |  | 0 | 0 | 403.66 |  | 403.66 | [16 empty] | 839 |  |  | 839 | 5 | 4195 |  |  |  | 0.000839 | 4195 | 0.096224 |  | If ECO-07 implemented and steam flow stopped when OA is above 70 degrees, reduce savings to $3,262 per year
| CRC-14 | 2014 | PI-01 EF-4 Motor operating at service factor | 401780 | Work Order 401780 in house labor: $117 | HVAC | 15 | COMPLETE | 2014-02-24 | Cowling | Mechanical |  | Q&S | 0 | 0 | 0 |  | 0 | 0 | 117 | 0 | 117 | [9 empty] | No calc | [11 empty] | No calc |  |  |  | 0 |  |  |  | May be fixed when we reduce exhaust airflow
| CRC-15 | 2014 | PI-02 Repair damaged ductwork | 401781 | Work Order 401781: in-house labor: $117 | HVAC | 15 | COMPLETE | 2014-02-24 | Cowling | Mechanical |  | Q&S | 0 | 0 | 0 |  | 0 | 0 | 117 | 0 | 117 | [9 empty] | No calc | [11 empty] | No calc |  |  |  | 0 |  |  |  | Mezz MER supply air
| CRC-16 | 2014 | PI-03 Abandoned Dryer Exhaust duct | 401782 | Work Order 401782 in-house labor: $117 | HVAC | 20 | COMPLETE | 2014-02-24 | Cowling | Mechanical |  | Q&S | 0 | 0 | 0 |  | 0 | 0 | 117 | 0 | 117 | [9 empty] | No calc | [11 empty] | No calc |  |  |  | 0 |  |  |  | From Women's Locker Room
| CRC-17 | 2014 | PI-04 AHU-2 OA and RA Broken Dampers | 365838 | MMC Invoice 204030775: $9391.38 | HVAC | 15 | COMPLETE | 2013-07-30 | Cowling | Mechanical |  | Q&S | 0 | 0 | 0 |  | 0 | 0 | 9391.38 | 0 | 9391.38 | [9 empty] | No calc | [11 empty] | No calc |  |  |  | 0 |  |  |  | Dampers are broken, replace these and actuators
| CRC-18 | 2014 | PI-05 AHU-3 OA, RA, Relief Air Dampers non-responsive | 365839 | MMC Invoice 204030596: $4941.82 MMC Invoice 204030782: $4981.22 | HVAC | 10 | COMPLETE | 2013-07-16 | Cowling | Mechanical |  | Q&S | 0 | 0 | 0 |  | 0 | 0 | 9923.04 | 0 | 9923.04 | [9 empty] | No calc | [11 empty] | No calc |  |  |  | 0
| CRC-19 | 2014 | PI-06 No Airflow to Pool Lobby through Reheat Coil RHC-6 ducts | 401783 | Work Order in-house labor: $175.50 | HVAC | 15 | COMPLETE | 2014-02-24 | Cowling | Pool Lobby |  | Q&S | 0 | 0 | 0 |  | 0 | 0 | 175.5 | 0 | 175.5 | [9 empty] | No calc | [11 empty] | No calc |  |  |  | 0
| CRC-20 | 2014 | PI-07 (ADDED BY CARLETON): AHU-1 Replace OA and RA Dampers | 365837 | MMC Invoice 204030595: $6458.96 | HVAC | 15 | COMPLETE | 2013-07-16 | Cowling | Mechanical |  | Carleton College | 0 | 0 | 0 |  | 0 | 0 | 6458.96 | 0 | 6458.96 | [26 empty] | 0
| CRC-21 | PENDING | ECO-12 Pool cover |  |  | HVAC | 20 | Quotes rec'd; decision pending |  | Cowling | Lower Level |  | Q&S | 10350 | 0 | 10350 |  | 0 | 0 | 0 | 0 | 0 | [16 empty] | 62 |  |  | 62 | 5 | 310 |  |  |  | 6.2e-05 | 310 | 0 |  | Includes ventilation air reduction, water use reduction, water heating reduction.
| CRC-22 | N/A | ECO-05 Low flow faucets |  |  | Water |  | Not Selected | N/A | Cowling | All |  | Q&S | 4140 | 0 | 4140 |  | 0 | 0 | 1911-05-02 | 0 | 1911-05-02 | [16 empty] | 6 |  |  |  | 1900-01-04 | 1900-01-29 |  |  |  | 6e-06 | 1900-01-29 | 1900-05-17
| CRC-23 | N/A | ECO-07 Valve off steam flow to Mezz mechanical room in Summer |  |  | HVAC |  | Not Selected | N/A | Cowling | Mechanical |  | Q&S | 3025 | -423 | 2602 |  | 0 | 0 | 1908-04-12 | -423 | 1907-02-14 | [16 empty] | 85 |  |  |  | 1900-01-04 | 1901-02-28 |  |  |  | 8.5e-05 | 1901-02-28 | 1900-01-05 02:56
| CRC-24 | N/A | ECO-14 Programmable Tstat for DX RTU |  |  | HVAC |  | Not Selected | N/A | Cowling | Roof |  | Q&S | 276 | -39 | 237 |  | 0 | 0 | 1900-10-02 | -39 | 1900-08-24 | [7 empty] | 1902-04-28 | 0.07 | 1900-02-27 10:19 | [15 empty] | 1900-01-01 21:31 | 1900-02-27 10:19 | 1900-01-02 23:43 |  | Allows for unoccupied setback control (max up to 80 degrees when unoccupied)
|  | Rec Center Audit: Dunham Engineering | [15 empty] | 0 | 0 | 3276.58 | 0 | 3276.58 | [7 empty] | 49317 |  | 3452.19 | [9 empty] | 3100.0014 |  | 2325.001 |  |  |  | 168.2699 | 5777.191 | 0.60037
| RC-1 | 2014 | ECM 1 Fix failed sensors | 370071 | Work Order in-house labor ($351) Siemens Invoice 5442831863 ($215) | HVAC | 10 | COMPLETE | 2013-09-03 | Rec Center | Various |  | Dunham | 2000 | 0 | 2000 |  | 0 | 0 | 566 | 0 | 566 | [25 empty] | 0 | 0 |  |  | AHU-1 CO2 had wrong slope/intercept, AHU-1 return air RH sensor will get checked on 4/01/14, building P transducer at RE-2 and AHU-4 were fixed (Siemens invoice), remaning items were fixed when we replaced brittle VAV tubing (see ECM-4)
| RC-2 | 2014 | ECM 2 Modify locker room exhaust to avoid negative building pressure | 370072 | MMC invoice 20428684: $900.82 (split btwn Rec & Cowling) MMC TAB report dated 1/01/14 (Job #20428684) | HVAC | 10 | COMPLETE | 2014-01-20 | Rec Center | Locker Room |  | Dunham | 1500 | -975 | 525 |  | 0 | 0 | 900.83 |  | 900.83 | [7 empty] | 13785 | 0.07 | 964.95 | 2.5 | [14 empty] | 47.0344 | 964.95 | 0.93355
| RC-3 | 2014 | ECM 3 Modify AHU-1 and AHU-2 control sequence | 370073 | Work Order in-house labor ($58.50) Mulcahy invoice 251220 - replace control boards $1020 | HVAC | 20 | COMPLETE | 2014-01-09 | Rec Center | Field House |  | Dunham | 3750 | -978 | 2772 |  | 0 | 0 | 1078.5 |  | 1078.5 | [7 empty] | 12922 | 0.07 | 904.54 | 3.6 | [14 empty] | 44.0899 | 904.54 | 1.1923
| RC-4 | 2014 | ECM 4 Fix AHU-3 VAV flow issues | 370076 | Work Order in-house labor ($351) | HVAC | 15 | COMPLETE | 2013-08-06 | Rec Center | Offices |  | Dunham | 3000 | -2182 | 818 |  | 0 | 0 | 351 |  | 351 | [7 empty] | 22195 | 0.07 | 1553.65 | 1.5 | [14 empty] | 75.7293 | 1553.65 | 0.22592 |  | Tubing that picked up the TEC from the VAV boxes was brittle - changed tubing on all VAV boxes; couldn’t sense it so would open VAV's 100% and over-pressurize the building
| RC-5 | 2014 | ECM 5 Fix OA entering through relief duct | 372306 | Work Order in-house labor ($58.50) | HVAC | 10 | COMPLETE | 2014-01-09 | Rec Center | Mechanical |  | Dunham | 0 | 0 | 0 |  | 0 | 0 | 58.5 |  | 58.5 | [7 empty] | 0 | 0.07 | 0 | 0 | [14 empty] | 0 | 0
| RC-6 | 2014 | ECM 6 Lower AHU-3 temperature setpoint | 372305 | Work Order in-house labor ($58.50) - already in PPCL | HVAC | 15 | COMPLETE | 2014-01-09 | Rec Center | Offices |  | Dunham | 0 | -225 | -225 |  | 0 | 0 | 58.5 |  | 58.5 | [16 empty] | 56.549 | 75% |  | 0.00075399 | 0.669 | 0.00050442 |  |  |  | 5.6549e-05 | 0.00050442
| RC-7 | 2014 | ECM 8 Restore OA flow through heat recovery coil | 372315 | Work Order in-house labor ($117) | HVAC | 10 | COMPLETE | 2014-01-09 | Rec Center | Mechanical |  | Dunham | 250 | -942 | -692 |  | 0 | 0 | 117 |  | 117 | [7 empty] | 415 | 0.07 | 29.05 | 4 | 14.7 |  |  |  |  | 216.8443 | 70% |  | 3100 | 0.75 | 2325 |  |  |  | 1.4162 | 2354.05 | 0.049702
| RC-8 | 2014 | ECM 9 Lower AHU-3 SA temperature setpoint | 372316 | Work Order in-house labor ($58.50) - already in PPCL | HVAC | 15 | COMPLETE | 2014-01-09 | Rec Center | Offices |  | Dunham | 0 | -207 | -207 |  | 0 | 0 | 58.5 |  | 58.5 | [16 empty] | 52.0846 | 75% |  | 0.00069446 | 0.669 | 0.00046459 |  |  |  | 5.2085e-05 | 0.00046459
| RC-9 | 2014 | ECM 10 Raise heating water temp setpoints to reduce pumping energy | 372317 372319 | Work Order in-house labor ($29.25) | HVAC | 15 | COMPLETE | 2014-01-09 | Rec Center | Mechanical |  | Dunham | 0 | 0 | 0 |  | 0 | 0 | 29.25 | 0 | 29.25 | [25 empty] | 0 | 0
| RC-10 | PENDING | ECM 11 Replace steam meter |  |  | Meters | 20 | Future project |  | Rec Center | Mechanical |  | Dunham | 0 | 0 | 0 |  | 0 |  | TBD | 0 | 0 | [25 empty] | 0 | 0
| RC-11 | PENDING | ECM 14 Fix or replace CW meter | 372326 |  | Meters | 20 | Work Order submitted 9/16/13 |  | Rec Center | Mechanical |  | Dunham | 0 | 0 | 0 |  | 0 | 0 | TBD | 0 | 0 | [25 empty] | 0 | 0
| RC-12 | PENDING | ECM 12 Study Campus CW Distribution | 372323 | Work Order completed 1/9/14 ($58.50) | HVAC | 20 | Future project |  | Rec Center | Chilled Water |  | Dunham | 0 | 0 | 0 |  | 0 | 0 | 58.5 | TBD | 58.5 | [7 empty] | TBD | [17 empty] | 0 | 0 |  |  | Building CW pumps are often turned off since central CW pumps provide sufficient pressure; this indicates central pumps may be overworked and should be studied for optimum combination of central plant and building pumping energy
| RC-13 | N/A | ECM 7 Add VAV control to spaces converted to offices |  |  | HVAC |  |  | Not Selected | Rec Center | Offices |  | Dunham |  |  |  |  | N/A | N/A | N/A | 0 | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A
| RC-14 | N/A | ECM 13 Reduce or eliminate CW bypass flow |  |  | HVAC |  |  | Not Selected | Rec Center | Chilled Water |  | Dunham |  |  |  |  | N/A | N/A | N/A | 0 | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A | N/A
|  | West Gym Audit: Sebesta Blomberg Engineering | [15 empty] | 0 | 0 | 40978.393 | -1990.4 | 38987.993 | [7 empty] | 76610.06 |  | 5362.7042 | [9 empty] | 13627 |  | 19887.363 |  |  |  | 261.3935 | 14921.2872 | 8.3604
| WG-1 | 2014 | ECM 1a: AHU-1 and AHU-2 CO2 Control | 402063 403275 | Work order in-house labor-mech: $234 Work order in-house labor - elec: $1521, Material $72.50 = $1593.50 Mulcahy invoice 261096 VFDs: $2239.54 | HVAC | 10 | COMPLETE | 2014-03-31 | West Gym | Gymnasium |  | Sebesta Blomberg | 23350 | -2000 | 21350 |  | 0 | 0 | 4067.04 | -2000 | 2067.04 | [7 empty] | 27524 | 0.07 | 1926.68 | 7 | [8 empty] | 2263 | 0.669 | 1513.947 |  |  |  | 93.9119 | 3440.627 | 0.60077
| WG-2 | 2014 | ECM 1b: AHU-1 and 2, Replace Outside Air Dampers | N/A | MMC Invoice 204030598 ($4239.69) MMC Invoice 204030599 ($2731.48) | HVAC | 15 | COMPLETE | 2013-08-22 | West Gym | Mechanical |  | Carleton College | ECM1a | ECM1a | ECM1a |  | 0 | 0 | 6971.48 |  | 6971.48 | [7 empty] | ECM 1a | ECM 1a | ECM 1a | ECM 1a | [8 empty] | ECM 1a | ECM 1a | ECM 1a |  |  |  | ECM 1a |  | ECM 1a
| WG-3 | 2014 | (ADD): AHU-5, Replace Outside Air Dampers | N/A | MMC Invoice 204030601 ($2074.49) MMC Invoice 204030784 ($260.95) | HVAC | 15 | COMPLETE | 2013-08-22 | West Gym | Mechanical |  | Carleton College | 2335.44 | 0 | 0 |  | 0 | 0 | 2335.44 |  | 2335.44 | [26 empty] | 0
| WG-4 | 2014 | ECM 3 AHU-4 Turn Off During Unoccupied Mode and Replace OA damper | N/A | MMC Invoice 204030600 ($2,448.95) MMC Invoice 204030783 ($1,496.22) | HVAC | 15 | COMPLETE | 2013-08-22 | West Gym | Lobby / Office |  | Sebesta Blomberg | 2760 | 0 | 2760 |  | 0 | 0 | 3945.17 |  | 3945.17 | [7 empty] | 16090 | 0.07 | 1126.3 | 3 | [8 empty] | 465 | 0.669 | 311.085 |  |  |  | 54.8991 | 1437.385 | 2.7447
| WG-5 | 2015 | ECM 5 AHU-5 Replace Pool Unit (premium for AC) | Capital Project |  | HVAC | 30 | Summer 2014 capital project |  | West Gym | Pool |  | Sebesta Blomberg | 101850 |  |  | 800000 | 0 | 0 | 0 | 0 | 0 | [7 empty] | -13736 | 0.07 | -961.52 | -22 | [8 empty] | 10817 | 0.669 | 7236.573 |  |  |  | -46.8672 | 6275.053 | 0
| WG-6 | 2014 | ECM 12 Replace 21 x 250W Metal Halide (Over Pool) with LED; changed to induction lights (LED wouldn't work) | 375674 (test) | TRC Invoice $710.64 | Lighting | 15 | Scheduled for March / April 2014 |  | West Gym | Pool |  | Sebesta Blomberg | 9660 | 0 | 9660 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 17149 | 0.07 | 1200.43 | 4 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 58.5124 | 1200.43 | 0
| WG-7 | 2014 | ECM 13 Replace 12 x 65W CFL (Bleachers) | 376443 | TRC invoice J91343A-IN: $2,210 | Lighting | 15 | COMPLETE | 2014-02-06 | West Gym | Pool |  | Sebesta Blomberg | 3240 | -600 | 2640 |  | 0 | 0 | 2210 |  | 2210 | 12 | 12 | 780 | 516 | 5040 | 5040 | 0 | 1330.56 | 0.07 | 93.1392 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 4.5399 | 93.1392 | 23.7279 |  | Used TRC calcs in kwh comparison (Sebesta estimated 2160 kwh saved)
| WG-8 | 2014 | ECM 14 replace 14 x 300W Pool Lights | 366985 | Work order in-house labor: $146.25 Werner LEV adapter Invoice S7494702.001: $48.28 Werner LED lamps Invoice S7494702.001: $573.68 | Lighting | 15 | COMPLETE | 2013-06-18 |  | Pool |  | Sebesta Blomberg | 7560 | -700 | 6860 |  | 0 | 0 | 768.21 |  | 768.21 | [7 empty] | 15266 | 0.07 | 1068.62 | 3 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 52.0876 | 1068.62 | 0.71888
| WG-9 | 2014 | ECM 15 Replace Exit Signs | 376682 | TRC invoice J91434A-IN: $2,995 | Lighting | 15 | COMPLETE | 2014-03-27 | West Gym | All |  | Sebesta Blomberg | 1215 | -90 | 1125 |  | 0 | 0 | 2995 |  | 2995 | 17 | 17 | 256 | 10 | 8761.7188 | 8900 | -138.2812 | 2154 | 0.07 | 150.78 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 7.3494 | 150.78 | 19.8634 |  | Used TRC calcs from 12/09/13 quote
| WG-10 | 2014 | ECM 16 Occ Sensors: Men's Restrooms | 376681 | TRC Invoice J91437A-IN: $825 | Lighting | 15 | COMPLETE | 2014-02-28 | West Gym | Men's Restroom |  | Sebesta Blomberg | 150 | -30 | 120 |  | 0 | 0 | 885 |  | 885 | [7 empty] | 613 | 0.07 | 42.91 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 2.0916 | 42.91 | 20.6246
| WG-11 | 2014 | ECM 17 Occ Sensors: Women's Restrooms | 376684 | TRC Invoice J91433A-IN: $825 | Lighting | 15 | COMPLETE | 2014-02-28 | West Gym | Women's Restroom |  | Sebesta Blomberg | 150 | -30 | 120 |  | 0 | 0 | 885 |  | 885 | [7 empty] | 611 | 0.07 | 42.77 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 2.0847 | 42.77 | 20.6921
| WG-12 | 2014 | ECM 18 Occ Sensors: Men's Locker Room (ADD: fixture replacements from circle line to 4' T8s; added laundry and custodial areas) | 376685 | TRC invoice J91432A-IN: $4815 | Lighting | 15 | COMPLETE | 2014-03-21 | West Gym | Men's Locker Room |  | Sebesta Blomberg | 500 | -60 | 440 |  | 0 | 0 | 4815 |  | 4815 | various | 13 | 1984 | 2086 | 6552.4194 | 3748.8015 | 2803.6178 | 5180 | 0.07 | 362.6 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 17.6742 | 362.6 | 13.2791 |  | Used TRC before/after calcs since scope was expanded to replace existing fixtures.
| WG-13 | 2014 | ECM 19 Occ Sensors: Women's Locker Room (ADD: replace circle line fixtures with T8s) | 376686 | TRC invoice J91436A-IN: $5,845 | Lighting | 15 | COMPLETE | 2014-03-21 | West Gym | Women's Locker Room |  | Sebesta Blomberg | 500 | -60 | 440 |  | 0 | 0 | 5845 |  | 5845 | various | 21 | 1303 | 903 | 6550.2686 | 3744.186 | 2806.0826 | 5154 | 0.07 | 360.78 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 17.5854 | 360.78 | 16.201 |  | Used TRC before/after calcs since scope was expanded to replace existing fixtures.
| WG-14 | 2014 | ECM 20 Occ Sensors: Women's Varsity (ADD: replace 2 circle line fixtures with one 2L T8 4' wraps) | 376687 | TRC invoice ?? $640 | Lighting | 15 | COMPLETE - have quote, need invoice | 2014-03-21 | West Gym | Women's Locker Room |  | Sebesta Blomberg | 250 | -30 | 220 |  | 0 | 0 | 640 |  | 640 | 2 | 1 | 468 | 449 | 6553.4188 | 3590.2004 | 2963.2184 | 1455 | 0.07 | 101.85 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 4.9645 | 101.85 | 6.2838 |  | Used TRC before/after calcs since scope was expanded to replace existing fixtures.
| WG-15 | 2014 | ECM 21 Occ Sensors: Trainer's Room | 376688 | TRC invoice J91439A-IN: $995 | Lighting | 15 | COMPLETE | 2014-02-28 | West Gym | Trainer Room |  | Sebesta Blomberg | 170 | -15 | 155 |  | 0 | 0 | 995 |  | 995 | [7 empty] | 459 | 0.07 | 32.13 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 1.5661 | 32.13 | 30.9679
| WG-16 | 2014 | ECM 22 Replace Ext. Light, Add Photocell | 376689 | TRC invoice J91434A-IN: $2995 | Lighting | 5 | COMPLETE - have quote, need invoice | 2014-02-28 | West Gym | Exterior doors |  | Sebesta Blomberg | 540 | -73 | 467 |  | 0 | 0 | 2995 |  | 2995 | 17 | 17 | 256 | 10 | 8761.7188 | 8900 | -138.2812 | 2154 | 0.07 | 150.78 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 7.3494 | 150.78 | 19.8634 |  | Used TRC calcs from 12/09/13 quote
| WG-17 | 2014 | ECM 23 Replace Entry Lights | 376442 | TRC Quote dated 12/03/13: $355 | Lighting | 15 | COMPLETE - have quote, need invoice | 2014-02-06 | West Gym | Entry vestibule |  | Sebesta Blomberg | 270 | -30 | 240 |  | 0 | 0 | 355 | 9.6 | 364.6 | 2 | 2 | 186 | 24 | 8750 | 4375 | 4375 | 1522.5 | 0.07 | 106.575 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 5.1948 | 106.575 | 3.4211 |  | TRC calcs assume lights are on 24/7, Sebesta assumes 12 hrs/day - with photocell, reduces lights to 12 hrs/ dy.
| WG-18 | 2014 | ECM 28 Replace Sink Aerators | 402062 | WO in-house labor/materials: $271.05 | Water | 20 | COMPLETE |  | West Gym | Restrooms / Locker Rooms |  | Sebesta Blomberg | 230 | 0 | 230 |  | 0 | 0 | 271.053 | 0 | 271.053 | [7 empty] | 0 | 0.07 | 0 | 0 | [8 empty] | 82 | 0.669 | 54.858 |  |  |  | 0 | 54.858 | 4.941
| WG-19 | PENDING | ECM 7 Install Pool Cover |  |  | HVAC | 20 | Quotes rec'd; decision pending |  | West Gym | Pool |  | Sebesta Blomberg | 11850 | 0 | 11850 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0.07 | 0 | 0 | [8 empty] | 4068 | 0.669 | 2721.492 |  |  |  | 0 | 2721.492 | 0
| WG-20 | PENDING | ECM 8 Solar Pool Heater |  |  | HVAC | 25 |  |  | West Gym | Pool |  | Sebesta Blomberg | 345000 |  |  |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | -10800 | 0.07 | -756 | 0 | [8 empty] | 8853 | 0.669 | 5922.657 |  |  |  | -36.8496 | 5166.657 | 0
| WG-21 | PENDING | ECM 9 Add Concession Vending Machine Control |  |  | Power | 10 |  |  | West Gym | Upstairs Lobby |  | Sebesta Blomberg | 230 |  |  |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1537 | 0.07 | 107.59 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 5.2442 | 107.59 | 0
| WG-22 | PENDING | ECM 10a Add Vending Machine Control |  |  | Power | 10 |  |  | West Gym | Lower Level |  | Sebesta Blomberg | 230 |  |  |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1808 | 0.07 | 126.56 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 6.1689 | 126.56 | 0
| WG-23 | PENDING | ECM 10b Delamp Vending Machine |  |  | Power | 10 | Decision pending |  | West Gym | Lower Level |  | Sebesta Blomberg | 5 | 0 | 5 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1139 | 0.07 | 79.73 | 0 | [8 empty] | 0 | 0.669 | 0 |  |  |  | 3.8863 | 79.73 | 0
| WG-24 | PENDING | ECM 24 Steam Study |  |  | HVAC | 10 |  |  | West Gym | Mechanical |  | Sebesta Blomberg | 3340 | 0 | 3340 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0.07 | 0 | 0 | [8 empty] | 3179 | 0.669 | 2126.751 |  |  |  | 0 | 2126.751 | 0
| WG-25 | N/A | ECM 1c: Add nine destratification fans in gym | 402064 |  | HVAC | 15 |  | Not Selected | West Gym | Mechanical |  | Carleton College | ECM1a | ECM1a | ECM1a | [13 empty] | ECM 1a | ECM 1a | ECM 1a | ECM 1a | [8 empty] | ECM 1a | ECM 1a | ECM 1a |  |  |  | ECM 1a | #VALUE! | ECM 1a
| WG-26 | N/A | ECM 2 AHU-3 Seal Outside Air Ductwork | 402060 |  | HVAC | 15 | WO submitted 2/15/14 | Not Selected | West Gym | Wrestling Room |  | Sebesta Blomberg | 0 | 0 | 0 |  | 0 | 0 | 350 | 0 | 350 | [7 empty] | 0 | 0.07 | 0 | 0 | [8 empty] | 146 | 0.669 | 97.674 |  |  |  | 0 | 97.674 | 3.5833 |  | Unit is not in use as of the time of this audit
| WG-27 | N/A | ECM 4a AHU-4 Add CO2 Control | 402059 |  | HVAC | 10 | WO submitted 2/15/14 | Not Selected | West Gym | Lobby / Office |  | Sebesta Blomberg | 2760 | 0 | 2760 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 172 | 0.07 | 12.04 | 1 | [8 empty] | 415 | 0.669 | 277.635 |  |  |  | 0.58686 | 289.675 | 0 |  | AHU-4 only services offices /conference in summer, serves three different zones so CO2 sensor placement is difficult and this ECM is not practical in this application
| WG-28 | N/A | ECM 4b Outside Air Rebalancing | 402058 |  | HVAC | 10 | WO submitted 2/15/14 | Not Selected | West Gym | Lobby / Office |  | Sebesta Blomberg | 600 | 0 | 600 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 98 | 0.07 | 6.86 | 0 | [8 empty] | 1249 | 0.669 | 835.581 |  |  |  | 0.33438 | 842.441 | 0 |  | Are there code issues with CO2 sensor if we don't meet minimum cfm?
| WG-29 | N/A | ECM 6 Install Energy Recovery Unit for Locker Rooms | 402057 |  | HVAC | 15 | WO submitted 2/15/14 | Not Selected | West Gym | Locker Room |  | Sebesta Blomberg |  |  |  |  | N/A | N/A | N/A | 0 | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | -19897 | N/A | N/A | -4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 7354 | N/A | N/A |  |  |  | N/A | #VALUE! | N/A | N/A | Payback too long
| WG-30 | N/A | ECM 11 Replace Ice Machine |  |  | Power | 15 |  | Not Selected | West Gym | Lower Level |  | Sebesta Blomberg |  |  |  |  | N/A | N/A | N/A | 0 | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 460 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A |  |  |  | N/A | #VALUE! | N/A | N/A
| WG-31 | N/A | ECM 25 Replace Shower Heads |  |  | Water | 20 |  | Not Selected | West Gym | Men's / Women's Locker Rooms |  | Sebesta Blomberg | 3220 | 0 | 3220 |  | 3220 | 0 | 0 | 0 | 3220 | [7 empty] | 0 | 0.07 | 0 | 0 | [8 empty] | 3461 | 0.669 | 2315.409 |  |  |  | 0 | 2315.409 | 1.3907
| WG-32 | N/A | ECM 26 Replace Toilet Fixtures |  |  | Water | 20 |  | Not Selected | West Gym | Restrooms / Locker Rooms |  | Sebesta Blomberg |  |  |  |  | N/A | N/A | N/A | 0 | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 0 | N/A | N/A |  |  |  | N/A | #VALUE! | N/A | N/A
| WG-33 | N/A | ECM 27 Replace Urinal Fixtures |  |  | Water | 20 |  | Not Selected | West Gym | Men's Restroom / Locker Room |  | Sebesta Blomberg |  |  |  |  | N/A | N/A | N/A | 0 | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 0 | N/A | N/A |  |  |  | N/A | #VALUE! | N/A | N/A
|  | Hulings Hall | [15 empty] | 0 | 0 | 0 | 0 | 0 | [7 empty] | 371784 |  | 31015 | Peak | [8 empty] | 26069 |  | 15601.8218 |  |  |  | 1268.527 | 46616.8218 | 4.1312
| HH-1 | PENDING | Modify laboratory air change rates by reducing ventilation requiremetns to meet current building codes and standards to AHUs -1,2 & 3 |  |  |  | 10 |  |  | Hulings Hall |  |  | Siemens | 85720 |  | 85720 | [13 empty] | 119222 | 0.071 | 8715 | [9 empty] | 27495 | 0.79978 | 16497 |  |  |  | 406.7855 | 25212 | 3.4
| HH-2 | PENDING | Implement common area lighting controls with scheduled operation |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 8000 |  | 8000 | [13 empty] | 8158 | 0.071 | 596 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 27.8351 | 596 | 8.6
| HH-3 | PENDING | Install daylighting controls and occupancy sensors to classrooms, restrooms, and offices |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 21300 |  | 21300 | [13 empty] | 23592 | 0.071 | 2490 | [9 empty] | -320 | 0.79978 | -252 |  |  |  | 80.4959 | 2238
| HH-4 | PENDING | Add supply air temperature reset control to AHU -1 |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 400 |  | 400 | [13 empty] | 0 | 0.071 | 0 | [9 empty] | 100 | 0.79978 | 81 |  |  |  | 0 | 81
| HH-5 | PENDING | Add supply air temperature reset control to AHU -2 |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 400 |  | 400 | [13 empty] | 0 | 0.071 | 0 | [9 empty] | 420 | 0.79978 | 339 |  |  |  | 0 | 339 | 1.1799
| HH-6 | PENDING | Add supply air temperature reset control to AHU -3 |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 400 |  | 400 | [13 empty] | 0 | 0.071 | 0 | [9 empty] | 420 | 0.79978 | 339 |  |  |  | 0 | 339 | 1.1799
| HH-7 | PENDING | Add static pressure reset control to AHU-1 |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 540 |  | 540 | [13 empty] | 2112 | 0.071 | 175 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 7.2061 | 175 | 3.0857
| HH-8 | PENDING | Add static pressure reset control to AHU-2 |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 540 |  | 540 | [13 empty] | 7002 | 0.071 | 579 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 23.8908 | 579 | 0.93264
| HH-9 | PENDING | Add static pressure reset control to AHU-3 |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 540 |  | 540 | [13 empty] | 7002 | 0.071 | 579 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 23.8908 | 579 | 0.93264
| HH-10 | PENDING | Add variable frequency drive (VFD) to heat recovery pump |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 11000 |  | 11000 | [13 empty] | 14413 | 0.071 | 1275 | [9 empty] | 10 | 0.79978 | 239 |  |  |  | 49.1772 | 1514 | 7.2
| HH-11 | PENDING | Upgrade Greenhouse E, F, G and Growth Room 1, 2, 3 lighting fixtures to high efficiency induction lighting fixtures |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 26500 |  | 26500 | [13 empty] | 163347 | 0.071 | 14445 | [9 empty] | -3770 | 0.79978 | -3012 |  |  |  | 557.34 | 11433 | 2.3179
| HH-12 | PENDING | Reduce dynamic head of primary hot water pump |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 350 |  | 350 | [13 empty] | 3817 | 0.071 | 279 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 13.0236 | 279 | 1.2545
| HH-13 | PENDING | Reduce dynamic head of primary heat recovery pump |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 350 |  | 350 | [13 empty] | 3817 | 0.071 | 279 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 13.0236 | 279 | 1.2545
| HH-14 | PENDING | Replace primary domestic hot water heater with high efficiency condensing unit of equivalent size |  |  |  | 25 |  |  | Hulings Hall |  |  | Siemens | 25000 |  | 25000 | [13 empty] | 0 | 0.071 | 0 | [9 empty] | 1714 | 0.79978 | 1370.8218 |  |  |  | 0 | 1370.8218 | 18.2372
| HH-15 | PENDING | Add static pressure reset control to all VFD controlled exhaust fans |  |  |  | 15 |  |  | Hulings Hall |  |  | Siemens | 4860 |  | 4860 | [13 empty] | 19302 | 0.071 | 1603 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 65.8584 | 1603 | 3.0318
| HH-16 | PENDING | [7 empty] | Hulings Hall |  |  | Siemens |  |  | 0 | [14 empty] | 0.071 | 0 | [10 empty] | 0.79978 | 0 |  |  |  | 0 | 0 | #DIV/0!
| HH-Maint1 | 2015 | Replace or install new valves on VAV 104, 304, 328 | [6 empty] | Hulings Hall |  |  | Siemens |  |  | 0 | [13 empty] | 0.071 | 0 | [9 empty] | 0.79978 | 0 |  | 0 | #DIV/0!
| HH-Maint2 | 2015 | Replace fume hood magnetic sahses with 2-position switches | [6 empty] | Hulings Hall |  |  | Siemens |  |  | 0 | [13 empty] | 0.071 | 0 | [9 empty] | 0.79978 | 0 |  | 0 | #DIV/0!
|  | Mudd Hall | [15 empty] | 0 | 0 | 0 | 0 | 0 | [7 empty] | 181377 |  | 12877.767 | [9 empty] | 9443 |  | 7552.3166 |  |  |  | 618.8583 | 20430.0836 | 7.0971
| MH-1 | PENDING | Modify laboratory air change rates by reducing ventilation requirements to meet current building codes and standards to AHUs -5,6 |  |  |  | 10 |  |  | Mudd Hall |  |  | Siemens | 44900 |  | 44900 | [13 empty] | 31228 | 0.071 | 2217.188 | [9 empty] | 7014 | 0.79978 | 5609.6525 |  |  |  | 106.5499 | 7826.8405 | 5.7367
| MH-2 | PENDING | Modify AHU-2 run-time schedule |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 400 |  | 400 | [13 empty] | 1250 | 0.071 | 88.75 | [9 empty] | 290 | 0.79978 | 231.936 |  |  |  | 4.265 | 320.686 | 1.2473
| MH-3 | PENDING | Modify AHU-3 run-time schedule |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 400 |  | 400 | [13 empty] | 1250 | 0.071 | 88.75 | [9 empty] | 290 | 0.79978 | 231.936 |  |  |  | 4.265 | 320.686 | 1.2473
| MH-4 | PENDING | Implement common area lighting controls with scheduled operation |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 8000 |  | 8000 | [13 empty] | 3358 | 0.071 | 238.418 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 11.4575 | 238.418 | 33.5545
| MH-5 | PENDING | Install daylighting controls and occupancy sensors to classrooms, restrooms, and offices |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 18900 |  | 18900 | [13 empty] | 20443 | 0.071 | 1451.453 | [9 empty] | -340 | 0.79978 | -271.925 |  |  |  | 69.7515 | 1179.528 | 16.0234
| MH-6 | PENDING | Add supply air temperature reset control to AHU-1 |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 400 |  | 400 | [14 empty] | 0.071 | 0 | [9 empty] | 70 | 0.79978 | 55.9846 |  |  |  | 0 | 55.9846 | 7.1448
| MH-7 | PENDING | Add supply air temperature reset control to AHU-4 |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 400 |  | 400 | [14 empty] | 0.071 | 0 | [9 empty] | 90 | 0.79978 | 71.9801 |  |  |  | 0 | 71.9801 | 5.5571
| MH-8 | PENDING | Add supply air temperature reset control to AHU-5 |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 400 |  | 400 | [14 empty] | 0.071 | 0 | [9 empty] | 200 | 0.79978 | 159.9559 |  |  |  | 0 | 159.9559 | 2.5007
| MH-9 | PENDING | Add supply air temperature reset control to AHU-6 |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 400 |  | 400 | [14 empty] | 0.071 | 0 | [9 empty] | 210 | 0.79978 | 167.9537 |  |  |  | 0 | 167.9537 | 2.3816
| MH-10 | PENDING | Add static pressure reset control to AHU-4 |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 540 |  | 540 | [13 empty] | 778 | 0.071 | 55.238 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 2.6545 | 55.238 | 9.7759
| MH-11 | PENDING | Add static pressure reset control to AHU-5 |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 540 |  | 540 | [13 empty] | 7820 | 0.071 | 555.22 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 26.6818 | 555.22 | 0.97259
| MH-12 | PENDING | Add static pressure reset control to AHU-6 |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 540 |  | 540 | [13 empty] | 8360 | 0.071 | 593.56 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 28.5243 | 593.56 | 0.90976
| MH-13 | PENDING | Add variable frequency drive (VFD) to hot water pumps (4 total) |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 28000 |  | 28000 | [13 empty] | 57652 | 0.071 | 4093.292 | [9 empty] | 1084 | 0.79978 | 866.9608 |  |  |  | 196.7086 | 4960.2528 | 5.6449
| MH-14 | PENDING | Add variable frequency drive (VFD) to hot water pumps (2 total) |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 18000 |  | 18000 | [13 empty] | 32026 | 0.071 | 2273.846 | [9 empty] | 535 | 0.79978 | 427.882 |  |  |  | 109.2727 | 2701.728 | 6.6624
| MH-15 | PENDING | Reduce dynamic head of primary heat recovery pumps (2 total) |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 700 |  | 700 | [13 empty] | 7834 | 0.071 | 556.214 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 26.7296 | 556.214 | 1.2585
| MH-16 | PENDING | Add static pressure reset control to all VFD controlled exhaust fans\ |  |  |  | 15 |  |  | Mudd Hall |  |  | Siemens | 2160 |  | 2160 | [13 empty] | 9378 | 0.071 | 665.838 | [9 empty] | 0 | 0.79978 | 0 |  |  |  | 31.9977 | 665.838 | 3.244
| MH-Maint1 | 2015 | Fix or replace damper on VAV box in Room 103
| MH-Maint2 | 2015 | Replace valve on VAV Box B74
|  | Olin Hall | [15 empty] | 0 | 0 | 0 | 0 | 0 | [7 empty] | 119162 |  | 9538.709 | [9 empty] | 5213 |  | 4169.2499 |  |  |  | 406.5807 | 13707.9589 | 6.557
| OH-1 | PENDING | FIM-1: Modify laboratory air change rates by reducing ventilation requirements to meet current building codes and standards and add demand control ventilation to AHU-1 |  |  | HVAC | 10 |  |  | Olin Hall | Mechanical |  | Siemens | 38700 |  | 38700 | [13 empty] | 40784 | 0.071 | 2981 | 6 | [8 empty] | 3626 | 0.79978 | 2900 |  |  |  | 139.155 | 5881 | 6.5805
| OH-2 | PENDING | Modify AHU-4 run time schedule |  |  |  | 15 |  |  | Olin Hall |  |  | Siemens | 400 |  | 400 | [13 empty] | 805 | 0.071 | 59 | 0 | [8 empty] | 200 | 0.79978 | 159.9559 |  |  |  | 2.7467 | 218.9559 | 1.8269
| OH-3 | PENDING | Implement common area lighting controls with scheduled operation |  |  |  | 15 |  |  | Olin Hall |  |  | Siemens | 8000 |  | 8000 | [13 empty] | 16607 | 0.071 | 1179.097 | 0 | [8 empty] | 0 | 0.79978 | 0 |  |  |  | 56.6631 | 1179.097 | 6.7849
| OH-4 | PENDING | Install daylighting controls and occupancy sensors to classrooms, restrooms, and offices |  |  |  | 15 |  |  | Olin Hall |  |  | Siemens | 24000 |  | 24000 | [13 empty] | 22394 | 0.071 | 2032 | 0 | [8 empty] | -380 | 0.79978 | -303.9162 |  |  |  | 76.4083 | 1728.0838 | 13.8882
| OH-5 | PENDING | Add supply air tempoarature reset control to AHU-1 |  |  |  | 15 |  |  | Olin Hall |  |  | Siemens | 800 |  | 800 | [13 empty] | 0 | 0.071 | 0 | 0 | [8 empty] | 1230 | 0.79978 | 983.7286 |  |  |  | 0 | 983.7286 | 0.81323
| OH-6 | PENDING | Add static pressure reset control to AHU-1 |  |  |  | 15 |  |  | Olin Hall |  |  | Siemens | 540 |  | 540 | [13 empty] | 19222 | 0.071 | 1595 | 0 | [8 empty] | 0 | 0.79978 | 0 |  |  |  | 65.5855 | 1595 | 0.33856
| OH-7 | PENDING | Add variable frequency drive (VFD) to hot water pumps (3 total) |  |  |  | 15 |  |  | Olin Hall |  |  | Siemens | 15500 |  | 15500 | [13 empty] | 17778 | 0.071 | 1581 | 0 | [8 empty] | 537 | 0.79978 | 429.4815 |  |  |  | 60.6585 | 2010.4815 | 7.7096
| OH-8 | PENDING | Add static pressure reset control to all VFD controlled exhaust fans. |  |  |  | 15 |  |  | Olin Hall |  |  | Siemens | 1620 |  | 1620 | [13 empty] | 1572 | 0.071 | 111.612 | 0 | [8 empty] | 0 | 0.79978 | 0 |  |  |  | 5.3637 | 111.612 | 14.5146
| OH-Maint1 | 2015 | Fix or replace discharge damper on VAV boxes in room 202, 305, 311, 329
|  | Gould Library Audit: Sebesta Blomberg Engineering | [13 empty] | 21070 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 122329 |  | 8685.359 | 22.1 |  | 112.047 | [5 empty] | 7771 | 0 |  | 46.626 |  |  |  | 417.3865 | 8844.032 | 3.6598
| GL-1 | PENDING | ECM 1: AHU-1, AHU-2, AHU-3 Remove inlet vanes to reduce static pressure |  |  |  |  | WO 418695 submitted on 3/11/15 |  |  |  |  | Sebesta | 1040 |  | 1040 | [13 empty] | 3636 | 0.071 | 258.156 | 1 | 5.07 | 5.07 | [5 empty] | -1675 |  | 0.006 | -10.05 |  |  |  | 12.406 | 253.176 | 4.1078
| GL-3 | PENDING | ECM 3: Discharge static pressure reset |  |  |  |  | 3/11/15: added to Siemens RFP |  |  |  |  | Sebesta | 1100 |  | 1100 | [13 empty] | 41784 | 0.071 | 2966.664 | 14 | 5.07 | 70.98 | [5 empty] | 9446 |  | 0.006 | 56.676 |  |  |  | 142.567 | 3094.32 | 0.35549
| GL-5 | PENDING | ECM 5: AHU-1, AHU-2, AHU-3 integrated economizer |  |  |  |  | 3/11/15: added to Siemens RFP; would base this on both enthalpy (<21) and outside temp (<75) |  |  |  |  | Sebesta | 1100 |  | 1100 | [13 empty] | 23184 | 0.071 | 1646.064 | 0 | 5.07 | 0 | [12 empty] | 79.1038 | 1646.064 | 0.66826
| GL-6 | PENDING | ECM 6: Occupancy light sensors for Blue Corner |  |  |  |  | MM to confirm if Blue Corner lights are on an independent circuit |  |  |  |  | Sebesta | 970 |  | 970 | [13 empty] | 829 | 0.071 | 58.859 | 0 | 5.07 | 0 | [12 empty] | 2.8285 | 58.859 | 16.4801
| GL-7 | PENDING | ECM 7: Remove special collections dehumidifier |  |  |  |  | Will wait on this; too political at the current time |  |  |  |  | Sebesta | 170 |  | 170 | [13 empty] | 9000 | 0.071 | 639 | 2 | 5.07 | 10.14 | [12 empty] | 30.708 | 649.14 | 0.26188
| GL-8 | PENDING | ECM 8: Elevator sleep mode, lamps and fans |  |  |  |  | MM will assign to Thyssenkrup |  |  |  |  | Sebesta | 1040 |  | 1040 | [13 empty] | 5661 | 0.071 | 401.931 | 0 | 5.07 | 0 | [12 empty] | 19.3153 | 401.931 | 2.5875
| GL-12 | PENDING | ECM 12: Replace sink aerators |  |  |  |  | MM will look into this; pipes don't get flushed as well with low-flow, causes clogs |  |  |  |  | Sebesta | 310 |  | 310 | [13 empty] | 3772 | 0.071 | 267.812 | 0 | 5.07 | 0 | [12 empty] | 12.8701 | 267.812 | 1.1575
| GL-13 | PENDING | ECM 13: Replace 12-13W CFL lights with LEDs, 4th Floor |  |  |  |  | MM will investigate |  |  |  |  | Sebesta | 410 |  | 410 | [13 empty] | 576 | 0.071 | 40.896 | 0.1 | 5.07 | 0.507 | [12 empty] | 1.9653 | 41.403 | 9.9027
| GL-14 | PENDING | ECM 14: Replace 12-16W CFL lights with LEDs, Entry |  |  |  |  | MM will investigate |  |  |  |  | Sebesta | 710 |  | 710 | [13 empty] | 360 | 0.071 | 25.56 | 0 | 5.07 | 0 | [12 empty] | 1.2283 | 25.56 | 27.7778
| GL-15 | PENDING | ECM 14: Replace 12-16W CFL lights with LEDs, Stairwell |  |  |  |  | MM will investigate |  |  |  |  | Sebesta | 1100 |  | 1100 | [13 empty] | 384 | 0.071 | 27.264 | 0 | 5.07 | 0 | [12 empty] | 1.3102 | 27.264 | 40.3462
| GL-16 | PENDING | ECM 14: Replace 12-16W CFL lights with LEDs, East Stairwell |  |  |  |  | MM will investigate |  |  |  |  | Sebesta | 1100 |  | 1100 | [13 empty] | 384 | 0.071 | 27.264 | 0 | 5.07 | 0 | [12 empty] | 1.3102 | 27.264 | 40.3462
| GL-17 | PENDING | ECM 13: Replace 19-60W MR16 Lights with LED, Athenaeum |  |  |  |  | MM - haven't found an LED fixture that works for this particular lighting style |  |  |  |  | Sebesta | 580 |  | 580 | [13 empty] | 671 | 0.071 | 47.641 | 0 | 5.07 | 0 | [12 empty] | 2.2895 | 47.641 | 12.1744
| GL-18 | PENDING | ECM 18: Reduce Lighting in 4th Floor Reference Room |  |  |  |  | Could remove bulbs - is dimming possible? Libe staff likes light levels, need to discuss w/ them |  |  |  |  | Sebesta | 6340 |  | 6340 | [13 empty] | 13944 | 0.071 | 990.024 | 2 | 5.07 | 10.14 | [12 empty] | 47.5769 | 1000.164 | 6.339
| GL-19 | 2015 | ECM 19: Reduce Lighting in 4th Floor Tech Room |  |  |  |  | COMPLETE in summer 2014 renovation; need to update calcs |  |  |  |  | Sebesta | 5100 |  | 5100 | [13 empty] | 18144 | 0.071 | 1288.224 | 3 | 5.07 | 15.21 | [12 empty] | 61.9073 | 1303.434 | 3.9127
| GL-2 | N/A | ECM 2: Replace AHU-1, AHU-2, AHU-3 cogged belts with synchronous belts and pulleys |  |  |  |  | 46 year payback is too long |  |  |  |  | Sebesta | 7590 |  | 7590 | [13 empty] | 2446 | 0.071 | 173.666 | 1 | 5.07 | 5.07 | [5 empty] | -1116 |  | 0.006 | 0 |  |  |  | 8.3458 | 178.736 | 42.4649
| GL-4 | N/A | ECM 4: AHU CO2 control / demand control ventilation |  |  |  |  | Overly complicates controls, maintenance; 20 year payback is too long |  |  |  |  | Sebesta | 8880 |  | 8880 | [13 empty] | 347 | 0.071 | 24.637 | 3 | 5.07 | 15.21 | [5 empty] | 70927 |  | 0.006 | 0 |  |  |  | 1.184 | 39.847 | 222.8524
| GL-9 | N/A | ECM 9: Modulate heating water pumps to maintain differential pressure |  |  |  |  | 23.7 year payback is too long |  |  |  |  | Sebesta | 1290 |  | 1290 | [13 empty] | 778 | 0.071 | 55.238 | 0 | 5.07 | 0 | [12 empty] | 2.6545 | 55.238 | 23.3535
| GL-10 | N/A | ECM 10: Replace water closets and urinal fixtures |  |  |  |  | 65 year payback is too long; will replace as needed for maintenance |  |  |  |  | Sebesta | 48880 |  | 48880 | [14 empty] | 0.071 | 0 | 0 | 5.07 | 0 | [12 empty] | 0 | 0 | #DIV/0!
| GL-11 | N/A | ECM 11: Replace electric water heater with heat pump |  |  |  |  | This heater is only used during steam plant shut-down; wait until utility master plan is further developed |  |  |  |  | Sebesta | 3270 |  | 3270 | [13 empty] | 3651 | 0.071 | 259.221 | 0 | 5.07 | 0 | [12 empty] | 12.4572 | 259.221 | 12.6147
|  | Sayles-Hill Audit: Sebesta Blomberg Engineering | [13 empty] | 55800 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 114784 |  | 8149.664 | 14 |  | 70.98 | 0 | 0 | 0 | 0 | 0 | 318041 | 103 | 0.644 | 1969.016 | 62 |  | 334.8 | 391.643 | 10524.46 | 2.9686
| SH-1 | PENDING | ECM 1: Clean dirty AHU-1 hot water heating coil |  |  |  |  | Work order 418711 submitted 3/11/15 |  |  |  |  | Sebesta | 140 |  | 140 | [13 empty] | 2211 | 0.071 | 156.981 | 0 | 5.07 | 0 | [5 empty] | -27 |  | 0.006 | -0.162 |  |  |  | 7.5439 | 156.819 | 0.89275
| SH-2 | PENDING | ECM 2: Integrated economizer |  |  |  |  | 3/11/15: added to Siemens RFP; would base this on both enthalpy (<21) and outside temp (<75) |  |  |  |  | Sebesta | 320 |  | 320 | [13 empty] | 7035 | 0.071 | 499.485 | 0 | 5.07 | 0 | [12 empty] | 24.0034 | 499.485 | 0.64066
| SH-3 | PENDING | ECM 3: AHU-1 and Constant Volume Kitchen Exhaust |  |  |  |  | MM/ ML to set up project |  |  |  |  | Sebesta | 9060 |  | 9060 | [13 empty] | 12686 | 0.071 | 900.706 | 2 | 5.07 | 10.14 | [5 empty] | 37213 |  | 0.006 | 223.278 |  |  |  | 43.2846 | 1134.124 | 7.9885
| SH-4 | PENDING | ECM 4: AHU-2 Integrated economizer |  |  |  |  | 3/11/15: added to Siemens RFP; would base this on both enthalpy (<21) and outside temp (<75) |  |  |  |  | Sebesta | 320 |  | 320 | [13 empty] | 4928 | 0.071 | 349.888 | 0 | 5.07 | 0 | [5 empty] | -8169 |  | 0.006 | -49.014 |  |  |  | 16.8143 | 300.874 | 1.0636
| SH-5 | PENDING | ECM 5: AHU-2 MAT Setpoint |  |  |  |  | Do this when the AHU is in economizer mode and min. OA is satisfied; Siemens has code for this |  |  |  |  | Sebesta | 320 |  | 320 | [13 empty] | 266 | 0.071 | 18.886 | 0 | 5.07 | 0 | [5 empty] | 122618 |  | 0.006 | 735.708 |  |  |  | 0.90759 | 754.594 | 0.42407
| SH-6 | PENDING | ECM 6: AHU2- Runtime Reduction | WO 418710 |  |  |  | COMPLETE | 2015-03-31 |  |  |  | Sebesta | 160 |  | 160 | [13 empty] | 6295 | 0.071 | 446.945 | 0 | 5.07 | 0 | [5 empty] | 65223 |  | 0.006 | 391.338 |  |  |  | 21.4785 | 838.283 | 0.19087
| SH-7 | PENDING | ECM 7: AHU-2 add VFD |  |  |  |  | Will bookstore be remodeled w/ Barnes & Nobel acquisition? 12 year payback on this. |  |  |  |  | Sebesta | 3790 |  | 3790 | [13 empty] | 1445 | 0.071 | 102.595 | 0 | 5.07 | 0 | [5 empty] | 34114 |  | 0.006 | 204.684 |  |  |  | 4.9303 | 307.279 | 12.3341
| SH-8 | PENDING | ECM 8: AHU-4 Integrated economizer |  |  |  |  | 3/11/15: added to Siemens RFP; would base this on both enthalpy (<21) and outside temp (<75) |  |  |  |  | Sebesta | 320 |  | 320 | [13 empty] | 15932 | 0.071 | 1131.172 | 0 | 5.07 | 0 | [5 empty] | 60347 |  | 0.006 | 362.082 |  |  |  | 54.36 | 1493.254 | 0.2143
| SH-9 | PENDING | ECM 9: AHU-4 Rest the Duct Static Pressure |  |  |  |  | Added to Siemens RFP, VFD is already running low; this won't save much energy |  |  |  |  | Sebesta | 1100 |  | 1100 | [13 empty] | 2071 | 0.071 | 147.041 | 1 | 5.07 | 5.07 | [5 empty] | 6043 |  | 0.006 | 36.258 |  |  |  | 7.0663 | 188.369 | 5.8396
| SH-10 | PENDING | ECM 10: AHU-4 Tune Chilled Water Valve |  |  |  |  | Will wait until CW is in use so we can see the changes during tuning |  |  |  |  | Sebesta | 160 |  | 160 | [13 empty] | 184 | 0.071 | 13.064 | 0 | 5.07 | 0 | [5 empty] | 679 |  | 0.006 | 4.074 |  |  |  | 0.62781 | 17.138 | 9.336
| SH-11 | PENDING | ECM 11: Replace sink aerators |  |  |  |  | MM will look into this; pipes don't get flushed as well with low-flow, causes clogs |  |  |  |  | Sebesta | 130 |  | 130 | [14 empty] | 0.071 | 0 | 0 | 5.07 | 0 | [6 empty] | 103 | 0.59 | 60.77 | 62 | 5.4 | 334.8 | 0 | 395.57 | 0.32864
| SH-13 | PENDING | ECM 13: Replace heating water pumps |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 8420 |  | 8420 | [13 empty] | 6684 | 0.071 | 474.564 | -1 | 5.07 | -5.07 | [12 empty] | 22.8058 | 469.494 | 17.9342
| SH-14 | PENDING | ECM 14: Add occupancy sensors in receiving area |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 870 |  | 870 | [13 empty] | 435 | 0.071 | 30.885 | 0 | 5.07 | 0 | [12 empty] | 1.4842 | 30.885 | 28.169
| SH-17 | PENDING | ECM 17: Replace Great Space lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 1600 |  | 1600 | [13 empty] | 6041 | 0.071 | 428.911 | 1 | 5.07 | 5.07 | [12 empty] | 20.6119 | 433.981 | 3.6868
| SH-18 | PENDING | ECM 18: Replace lower level Bookstore lighting with LED |  |  |  |  | Will bookstore be remodeled w/ Barnes & Nobel acquisition? 11 year payback on this. |  |  |  |  | Sebesta | 2170 |  | 2170 | [13 empty] | 2728 | 0.071 | 193.688 | 1 | 5.07 | 5.07 | [12 empty] | 9.3079 | 198.758 | 10.9178
| SH-19 | PENDING | ECM 19: Replace Bookstore storage lighting with LED |  |  |  |  | Will bookstore be remodeled w/ Barnes & Nobel acquisition? 11 year payback on this. |  |  |  |  | Sebesta | 2480 |  | 2480 | [13 empty] | 3248 | 0.071 | 230.608 | 1 | 5.07 | 5.07 | [12 empty] | 11.0822 | 235.678 | 10.5228
| SH-20 | PENDING | ECM 20: Replace Career Center lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 3630 |  | 3630 | [13 empty] | 6310 | 0.071 | 448.01 | 1 | 5.07 | 5.07 | [12 empty] | 21.5297 | 453.08 | 8.0118
| SH-21 | PENDING | ECM 21: Replace Main Level Bookstore lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 1280 |  | 1280 | [13 empty] | 5067 | 0.071 | 359.757 | 1 | 5.07 | 5.07 | [12 empty] | 17.2886 | 364.827 | 3.5085
| SH-23 | PENDING | ECM 23: Replace Main Level Entry lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 1800 |  | 1800 | [13 empty] | 2339 | 0.071 | 166.069 | 1 | 5.07 | 5.07 | [12 empty] | 7.9807 | 171.139 | 10.5178
| SH-24 | PENDING | ECM 24: Replace Corridor 140 lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 570 |  | 570 | [13 empty] | 1429 | 0.071 | 101.459 | 0 | 5.07 | 0 | [12 empty] | 4.8757 | 101.459 | 5.618
| SH-25 | PENDING | ECM 25: Replace Student Activities lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 2790 |  | 2790 | [13 empty] | 5652 | 0.071 | 401.292 | 1 | 5.07 | 5.07 | [12 empty] | 19.2846 | 406.362 | 6.8658
| SH-26 | PENDING | ECM 26: Replace Activity Center lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 1570 |  | 1570 | [13 empty] | 2923 | 0.071 | 207.533 | 1 | 5.07 | 5.07 | [12 empty] | 9.9733 | 212.603 | 7.3847
| SH-27 | PENDING | ECM 27: Replace Lounge Area 214, 216, 217 with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 2620 |  | 2620 | [13 empty] | 4677 | 0.071 | 332.067 | 1 | 5.07 | 5.07 | [12 empty] | 15.9579 | 337.137 | 7.7713
| SH-31 | PENDING | ECM 31: Replace Room 242 lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 530 |  | 530 | [13 empty] | 1234 | 0.071 | 87.614 | 0 | 5.07 | 0 | [12 empty] | 4.2104 | 87.614 | 6.0493
| SH-32 | PENDING | ECM 32: Replace Room 250, 251, 252, 253, 254 lighting with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 3900 |  | 3900 | [13 empty] | 7396 | 0.071 | 525.116 | 2 | 5.07 | 10.14 | [12 empty] | 25.2352 | 535.256 | 7.2862
| SH-34 | PENDING | ECM 34: Replace ten exterior 150W metal halide fixtures with LED |  |  |  |  | Summer 2015 project |  |  |  |  | Sebesta | 5750 |  | 5750 | [13 empty] | 5568 | 0.071 | 395.328 | 1 | 5.07 | 5.07 | [12 empty] | 18.998 | 400.398 | 14.3607
| SH-35 | PENDING | ECM 35: Add occupancy sensors to all restrooms |  |  |  |  | Summer 2015 project |  |  |  |  | Carleton
| SH-12 | N/A | ECM 12: Replace water closets and urnial fixtures |  |  |  |  | 65 year payback is too long; will replace as needed for maintenance |  |  |  |  | Sebesta | 28750 |  | 28750 | [14 empty] | 0.071 | 0 | 0 | 5.07 | 0 | [9 empty] | 111 | 5.4 | 599.4 | 0 | 599.4
| SH-15 | N/A | ECM 15: Add daylight sensors to Stairwell B |  |  |  |  | Fixture replacement does have sufficient payback at 71.6 years |  |  |  |  | Sebesta | 1240 |  | 1240 | [13 empty] | 248 | 0.071 | 17.608 | 0 | 5.07 | 0 | [12 empty] | 0.84618 | 17.608 | 70.4225
| SH-16 | N/A | ECM 16: Replace lower level corridor lighting with LED |  |  |  |  | 22 year payback, will wait until this is a maintenance issue to replace fixtures |  |  |  |  | Sebesta | 3440 |  | 3440 | [13 empty] | 2144 | 0.071 | 152.224 | 0 | 5.07 | 0 | [12 empty] | 7.3153 | 152.224 | 22.5983
| SH-28 | N/A | ECM 28: Replace Lounge Area 214 PAR lighting with LED |  |  |  |  | 46 year payback; will do this as needed for maintenance |  |  |  |  | Sebesta | 360 |  | 360 | [13 empty] | 111 | 0.071 | 7.881 | 0 | 5.07 | 0 | [12 empty] | 0.37873 | 7.881 | 45.6795
| SH-29 | N/A | ECM 29: Replace Lounge Area 217 PAR lighting with LED |  |  |  |  | 40.7 year payback; will do this as needed for maintenance |  |  |  |  | Sebesta | 370 |  | 370 | [13 empty] | 130 | 0.071 | 9.23 | 0 | 5.07 | 0 | [12 empty] | 0.44356 | 9.23 | 40.0867
| SH-30 | N/A | ECM 30: Replace Lounge Area 217 CFL lighting with LED |  |  |  |  | 25.9 year payback; will do this as needed for maintenance |  |  |  |  | Sebesta | 530 |  | 530 | [13 empty] | 292 | 0.071 | 20.732 | 0 | 5.07 | 0 | [12 empty] | 0.9963 | 20.732 | 25.5643
| SH-33 | N/A | ECM 33: Replace Computer Room lighting with LED |  |  |  |  | 23 year payback; will do this as needed for maintenance |  |  |  |  | Sebesta | 1880 |  | 1880 | [13 empty] | 1169 | 0.071 | 82.999 | 0 | 5.07 | 0 | [12 empty] | 3.9886 | 82.999 | 22.6509
| SH-22 | N/A | ECM 22: Replace Main Level Bookstore spotlighting with LED |  |  |  |  | 18 year payback; will do this as a sumemr maintenance project |  |  |  |  | Sebesta | 620 |  | 620 | [13 empty] | 483 | 0.071 | 34.293 | 0 | 5.07 | 0 | [12 empty] | 1.648 | 34.293 | 18.0795
|  | LDC Audit: Sebesta Blomberg Engineering | [13 empty] | 50770 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 116231 |  | 8252.401 | 23 |  | 116.61 | [5 empty] | 469110 | 0 |  | 2814.66 |  |  |  | 396.5802 | 11183.671 | 66.0487
| LDC-1 | PENDING | ECM 1: AHU-1, AHU-3, AHU-4 Kitchen exhaust optimization |  |  |  |  | MM/ML to outline project scope based on p. 47 Recommendations | [5 empty] | 21970 |  | 21970 | [13 empty] | 46461 | 0.071 | 3298.731 | 9 | 5.07 | 45.63 | [5 empty] | 431949 |  | 0.006 | 2591.694 |  |  |  | 158.5249 | 5936.055 | 3.7011
| LDC-2 | PENDING | ECM 2: AHU-3 Tune the heating valve |  |  |  |  | 3/11/15: added to Siemens RFP | [5 empty] | 120 |  | 120 | [14 empty] | 0.071 | 0 | 0 | 5.07 | 0 | [5 empty] | 28870 |  | 0.006 | 173.22 |  |  |  | 0 | 173.22 | 0.69276
| LDC-3 | PENDING | ECM 3: AHU-2 Tune the chilled water valve |  |  |  |  | 3/11/15: added to Siemens RFP; will do when CW is operating | [5 empty] | 120 |  | 120 | [13 empty] | 288 | 0.071 | 20.448 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 0.98266 | 20.448 | 5.8685
| LDC-4 | PENDING | ECM 4: AHU-2 reset the duct staitc pressure |  |  |  |  | 3/11/15: added to Siemens RFP | [5 empty] | 460 |  | 460 | [13 empty] | 1860 | 0.071 | 132.06 | 1 | 5.07 | 5.07 | [5 empty] | 3243 |  | 0.006 | 19.458 |  |  |  | 6.3463 | 156.588 | 2.9376
| LDC-5 | PENDING | ECM 5: AHU-2 Reset supply air temperature |  |  |  |  | 3/11/15: added to Siemens RFP | [5 empty] | 580 |  | 580 | [13 empty] | 714 | 0.071 | 50.694 | 0 | 5.07 | 0 | [5 empty] | 2596 |  | 0.006 | 15.576 |  |  |  | 2.4362 | 66.27 | 8.7521
| LDC-6 | PENDING | ECM 6: AHU-2 Integrated economizer |  |  |  |  | 3/11/15: added to Siemens RFP; would base this on both enthalpy (<21) and outside temp (<75) | [5 empty] | 230 |  | 230 | [13 empty] | 4833 | 0.071 | 343.143 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 16.4902 | 343.143 | 0.67027
| LDC-7 | PENDING | ECM 7: AHU-1 Tune the chilled water valve |  |  |  |  | 3/11/15: added to Siemens RFP; will do when CW is operating | [5 empty] | 120 |  | 120 | [13 empty] | 377 | 0.071 | 26.767 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 1.2863 | 26.767 | 4.4831
| LDC-8 | PENDING | ECM 8: AHU-1 Tune the supply fan VFD |  |  |  |  | 3/11/15: added to Siemens RFP | [5 empty] | 120 |  | 120 | [13 empty] | 2245 | 0.071 | 159.395 | 1 | 5.07 | 5.07 | [7 empty] | 0.006 | 0 |  |  |  | 7.6599 | 164.465 | 0.72964
| LDC-9 | PENDING | ECM 9: AHU-1 Reset the duct static pressure |  |  |  |  | 3/11/15: added to Siemens RFP | [5 empty] | 460 |  | 460 | [13 empty] | 1057 | 0.071 | 75.047 | 1 | 5.07 | 5.07 | [7 empty] | 0.006 | 0 |  |  |  | 3.6065 | 80.117 | 5.7416
| LDC-10 | PENDING | ECM 10: AHU-1 Reset supply air temperature |  |  |  |  | 3/11/15: added to Siemens RFP | [5 empty] | 580 |  | 580 | [13 empty] | 647 | 0.071 | 45.937 | 0 | 5.07 | 0 | [5 empty] | 2452 |  | 0.006 | 14.712 |  |  |  | 2.2076 | 60.649 | 9.5632
| LDC-11 | PENDING | ECM 11: AHU-1 Economizer |  |  |  |  | 3/11/15: added to Siemens RFP; would base this on both enthalpy (<21) and outside temp (<75) | [5 empty] | 230 |  | 230 | [13 empty] | 1165 | 0.071 | 82.715 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 3.975 | 82.715 | 2.7806
| LDC-12 | PENDING | ECM 12: Restroom exhaust fan is on 24/7, lock in w/ AHU-2 |  |  |  |  | MM/ML to set up as a summer | [5 empty] | 120 |  | 120 | [13 empty] | 6180 | 0.071 | 438.78 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 21.0862 | 438.78 | 0.27349
| LDC-15 | PENDING | ECM 15: Domestic water pump operates 24/7 |  |  |  |  | Summer 2015 project | [5 empty] | 350 |  | 350 | [13 empty] | 784 | 0.071 | 55.664 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 2.675 | 55.664 | 6.2877
| LDC-18 | PENDING | ECM 18: Replace 60 Watt multi-vapor exterior dock lights with LED |  |  |  |  | Summer 2015 project | [5 empty] | 350 |  | 350 | [13 empty] | 1689 | 0.071 | 119.919 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 5.7629 | 119.919 | 2.9186
| LDC-19 | PENDING | ECM 19: Replace second and third floor T8 lighting with LED |  |  |  |  | Summer 2015 project; will not replace w/ LEDs at this time but can add limits on the dimming system to conserve energy (need to recalculate payback) | [5 empty] | 24040 |  | 24040 | [13 empty] | 43653 | 0.071 | 3099.363 | 11 | 5.07 | 55.77 | [7 empty] | 0.006 | 0 |  |  |  | 148.944 | 3155.133 | 7.6193
| LDC-20 | PENDING | ECM 20: Sleep mode for elevator fan and lamps (change lamps to LED?) |  |  |  |  | Summer 2015 project | [5 empty] | 920 |  | 920 | [13 empty] | 4278 | 0.071 | 303.738 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 14.5965 | 303.738 | 3.0289
| LDC-21 | PENDING | ECM 21: Ice Machine exhaust fan operates 24/7; turn off when OAT is below 55 degrees and use rejected heat to warm the space |  |  |  |  | Add to Jeff Mason list
| LDC-13 | N/A | ECM 13: Heating water pumps 1 & 2 operate above 65 deg OAT |  |  |  |  | Most of our reheat is for make-up air; won't need reheat in summer - not a big energy saver (10 year payback); may self-correct if we do other ECMs, heating pumps may not need to run these pumps | [5 empty] | 460 |  | 460 | [13 empty] | 631 | 0.071 | 44.801 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 2.153 | 44.801 | 10.2676
| LDC-14 | N/A | ECM 14: Heating water pumps 1&2 modulate to maintain differential pressure, implement advanced control strategy |  |  |  |  | 31.6 year payback | [5 empty] | 4140 |  | 4140 | [13 empty] | 1870 | 0.071 | 132.77 | 0 | 5.07 | 0 | [7 empty] | 0.006 | 0 |  |  |  | 6.3804 | 132.77 | 31.1817
| LDC-16 | N/A | ECM 16: Remove pneumatic controls on AHUs |  |  |  |  | 41.3 year payback; will do this as maintenance is needed | [5 empty] | 22540 |  | 22540 | [13 empty] | 3024 | 0.071 | 214.704 | 0 | 5.07 | 0 | [5 empty] | 56696 |  | 0.006 | 340.176 |  |  |  | 10.3179 | 554.88 | 40.6214
| LDC-17 | N/A | ECM 17: Replace 13-year old dishwasher with more efficient model |  |  |  |  | 50+ year payback; will do this as maintenance is needed | [5 empty] | 66470 |  | 66470 | [13 empty] | 10000 | 0.071 | 710 | 0 | 5.07 | 0 | [5 empty] | 10000 |  | 0.006 | 60 |  |  |  | 34.12 | 770 | 86.3247
|  | Energy Club 2017 Lighting Audits | [13 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 211002 |  | 14981.14 | 0 |  | 0 | [5 empty] | 0 | 0 |  | 0 |  |  |  | 0 | 0 | 115.7
| EC-1 | 2017 | ECM 1: Installing sensors to non-residential bathrooms |  |  | Lighting controls | 15 |  |  | CMC |  |  |  | 4800 | [8 empty] | 10 |  | 2145 |  | 8760 |  |  | 18527 |  | 1315.45 | [17 empty] | 3.6
[10 empty] | Cowling |  |  |  | 3200 | [8 empty] | 19 |  | 1338 |  | 8760 |  |  | 11218 |  | 796.48 | [17 empty] | 4
[10 empty] | Facilities |  |  |  | 1600 | [8 empty] | 8 |  | 406 |  | 8760 |  |  | 3348 |  | 237.71 | [17 empty] | 6.7
[10 empty] | Laird Hall |  |  |  | 1600 | [8 empty] | 11 |  | 1220 |  | 8760 |  |  | 10398 |  | 738.27 | [17 empty] | 2.2
[10 empty] | LDC |  |  |  | 4800 | [8 empty] | 26 |  | 2435 |  | 8760 |  |  | 20646 |  | 1465.84 | [17 empty] | 3.3
[10 empty] | Rec Center |  |  |  | 3200 | [8 empty] | 34 |  | 2205 |  | 8760 |  |  | 18424 |  | 1308.11 | [17 empty] | 2.4
[10 empty] | Sayles Hill |  |  |  | 3200 | [8 empty] | 10 |  | 1092 |  | 8760 |  |  | 9300 |  | 660.27 | [17 empty] | 4.8
[10 empty] | West Gym |  |  |  | 1600 | [8 empty] | 10 |  | 1408 |  | 8760 |  |  | 12071 |  | 857.06 | [17 empty] | 1.9
| EC-2 | 2017 | ECM 2: Installing sensors to stairwells (open and semi-closed) | [6 empty] | Burton Hall |  |  |  | 600 | [8 empty] | 2 |  | 156 |  | 8760 |  |  | 1333 |  | 94.66 | [17 empty] | 6.3
[10 empty] | CMC |  |  |  | 2100 | [8 empty] | 7 |  | 492.2 |  | 8760 |  |  | 4140 |  | 293.94 | [17 empty] | 7.1
[10 empty] | Goodhue Hall |  |  |  | 300 | [8 empty] | 1 |  | 70.1 |  | 8760 |  |  | 597 |  | 42.42 | [17 empty] | 7.1
[10 empty] | Goodsell |  |  |  | 900 | [8 empty] | 3 |  | 204.8 |  | 8760 |  |  | 1720 |  | 122.15 | [17 empty] | 7.4
[10 empty] | LDC |  |  |  | 1800 | [8 empty] | 6 |  | 486.4 |  | 8760 |  |  | 4114 |  | 292.07 | [17 empty] | 6.2
[10 empty] | Musser Hall |  |  |  | 5700 | [8 empty] | 19 |  | 1337.6 |  | 8760 |  |  | 11401 |  | 809.48 | [17 empty] | 7
[10 empty] | Myers Hall |  |  |  | 4800 | [8 empty] | 16 |  | 1021.6 |  | 8760 |  |  | 8683 |  | 616.49 | [17 empty] | 7.8
[10 empty] | Nourse Hall |  |  |  | 3000 | [8 empty] | 10 |  | 1408 |  | 8760 |  |  | 12168 |  | 863.9 | [17 empty] | 3.5
[10 empty] | Sayles Hill |  |  |  | 4200 | [8 empty] | 14 |  | 1343.6 |  | 8760 |  |  | 11427 |  | 811.28 | [17 empty] | 5.2
[10 empty] | Severence Hall |  |  |  | 2700 | [8 empty] | 9 |  | 806 |  | 8760 |  |  | 6911 |  | 490.66 | [17 empty] | 5.5
[10 empty] | Watson Hall |  |  |  | 4800 | [8 empty] | 16 |  | 1126.4 |  | 8760 |  |  | 9601 |  | 681.67 | [17 empty] | 7
[10 empty] | Willis Hall |  |  |  | 4500 | [8 empty] | 15 |  | 1940 |  | 8760 |  |  | 16626 |  | 1180.48 | [17 empty] | 3.8
| EC-3 | 2017 | ECM 3: Installing sensors to tunnels | [6 empty] | Boliou |  |  |  | 5100 | [8 empty] | 17 |  | 1466.2 |  | 8760 |  |  | 12427 |  | 882.31 | [17 empty] | 5.8
[10 empty] | Cassat Hall |  |  |  | 3000 | [8 empty] | 10 |  | 704 |  | 8760 |  |  | 5922 |  | 420.44 | [17 empty] | 7.1
|  | Miscellaneous Projects | [15 empty] | 126596 | 100 | 545017.69 | -57558 | 571155.69 | [7 empty] | 860168.6048 |  | 60211.8023 | [9 empty] | 0 |  | 0 |  |  |  | 2919.1432 | 59888.635 | 5.5677
| CC-1 | 2010 | Lighting Retrofit: Library Fixture Replacement |  |  | Lighting | 20 | COMPLETE - fill in details | 2010-01-12 | Library | All except Reference and Rookery |  | Maintenance |  |  |  |  | 0 | 0 | 143250 | -5554 | 137696 | [7 empty] | 319377 | 0.07 | 22356.39 | 50.44 | [14 empty] | 1089.7143 | 22356.39 | 6.1591 |  | TRC notes say 523673 total kWh reduced to 204296 kWh (no detail provided)
| CC-2 | 2011 | Lighting Retrofit: Library Controls Installation |  |  | Lighting | 15 | COMPLETE - fill in details | 2010-08-24 | Library | All except Reference and Rookery |  | Maintenance |  |  |  |  | 0 | 0 | 144350 | -12782 | 131568 | [7 empty] | 0 | 0.07 | 0 | [15 empty] | 0 | 0
| CC-3 | 2011 | Window Replacement: Watson (capital) |  |  | Windows | 40 |  | 2011-08-15 | Watson Hall | Floors 2-7 |  | Maintenance |  |  |  |  | 0 | 0 | 0 |  | 0 | [25 empty] | 0 | 0
| CC-4 | 2012 | Boiler Tune-up: Boilers #2 and #3 |  |  | HVAC | 5 |  | 2012-03-20 | Facilities | Boiler House |  | Maintenance |  |  |  |  | 0 | 0 | 3339 | -500 | 2839 | [25 empty] | 0 | 0
| CC-5 | 2012 | Lighting Retrofit: Library Reference Room |  |  | Lighting | 20 | COMPLETE - fill in details | 2012-01-05 | Library | Reference Room |  | Maintenance |  |  |  |  | 0 | 0 | 91595 | -6046 | 85549 | 408 |  | 100 | 57.5 | 5892 | 5892 | 0 | 102167.28 | 0.07 | 7151.7096 | - | [14 empty] | 348.5948 | 7151.7096 | 11.962 |  | 58 of the 408 fixtures were T12 (106W) fixtures.
| CC-6 | 2012 | Residential Boiler Replacements (12) |  |  | HVAC | 30 | COMPLETE - fill in details | 2012-07-01 | Various | Basement |  | Maintenance |  |  |  |  | 0 | 0 |  | -1200 | -1200 | [13 empty] | 12 | [11 empty] | 0 | 0
| CC-7 | 2012 | Lighting Retrofit: West Gym |  |  | Lighting | 20 | COMPLETE - fill in details | 2012-07-09 | West Gym | Main Gym |  | Maintenance |  |  |  |  | 46041 | 0 | 0 | -2800 | 43241 | 70 |  | 295 | 234 | 5840 | 4088 | 1752 | 53634.56 | 0.07 | 3754.4192 | [15 empty] | 183.0011 | 3754.4192 | 11.5174
| CC-8 | 2013 | MH to T8: Cowling Locker Rooms | 364524 | TRC Invoice ?: $1,940 | Lighting | 15 | COMPLETE - Have quote, need invoice. | 2013-03-28 | Cowling | Men's / Women's Locker Rooms |  | Maintenance |  |  |  |  | 0 | 0 | 1940 | -726 | 1214 | [25 empty] | 0 | 0
| CC-9 | 2013 | PAR38 to LED: Cowling Pool (underwater) | 369720A | TRC invoice J90572A-IN: $1440 | Lighting | 5 | COMPLETE | 2013-08-20 | Cowling | Pool |  | Maintenance |  |  |  |  | 0 | 0 | 1440 |  | 1440 | 14 | 14 | 300 | 19.5 | 2000 | 2000 | 0 | 7854 | 0.07 | 549.78 | [15 empty] | 26.7978 | 549.78 | 2.6192
| CC-10 | 2013 | MH (100W) to LED PAR 38: Cowling Pool (ceiling) | 369720 | TRC invoice J90571A-IN: $2895 | Lighting | 5 | COMPLETE | 2013-08-20 | Cowling | Pool |  | Maintenance |  |  |  |  | 0 | 0 | 2895 |  | 2895 | 23 | 23 | 125 | 24 | 2000 | 2000 | 0 | 4646 | 0.07 | 325.22 | [15 empty] | 15.8522 | 325.22 | 8.9017
| CC-11 | 2013 | Steam to hot water: Evans Hall (capital) |  |  | HVAC | 80 |  | 2013-01-01 | Evans Hall | All |  | Capital |  |  |  | 1000000 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 0 | 0
| CC-12 | 2013 | Window Replacement: Evans Hall (capital) |  |  | Windows | 40 |  | 2013-01-01 | Evans Hall | Floors 1-4 |  | Capital |  |  |  | 350000 | 0 | 0 | 0 | -1879 | -1879 | [25 empty] | 0 | 0
| CC-13 | 2013 | Lighting Retrofit: Grounds Shop | 359169 | Cedar Lake invoice 49293: $2,235 | Lighting | 20 | COMPLETE - Carleton applied for rebate | 2012-12-28 | Grounds Shop | Grounds Shop |  | Maintenance | 2235 | 619 | -54 |  | 0 | 0 | 2235 |  | 2235 | [25 empty] | 0 | 0 |  |  | Retrofit existing 8-ft fixtures with 4-ft 4-lamp kits
| CC-14 | 2014 | Lighting Retrofit: LDC - TOTALS | capital project |  | Lighting | 20 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  |  |  | 0 | 0 | 129885 | -7058 | 122827 | See breakdown | See breakdown | See breakdown | See breakdown | See breakdown | See breakdown | See breakdown | See breakdown | See breakdown | See breakdown | [15 empty] | See breakdown | See breakdown
| CC-15 | 2014 | Lighting Retrofit: LDC 2x4 troffer | capital project |  | Lighting | 20 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -54 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 36 | 36 | 85 | 63 | 7300 | 7300 | 0 | 5781.6 | 0.07 | 404.712 | [15 empty] | 19.7268 | 404.712
| CC-16 | 2014 | Lighting Retrofit: LDC Ceiling Mount Occ. Sensor (>300W) | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -2800 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CC-17 | 2014 | Lighting Retrofit: LDC Ceiling Mount Occ. Sensor (50W-300W) | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -4470 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CC-18 | 2014 | Lighting Retrofit: LDC classroom T8 group #1 | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -48 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 48 | 48 | 67 | 46 | 4380 | 1750 | 2630 | 10222.08 | 0.07 | 715.5456 | [15 empty] | 34.8777 | 715.5456
| CC-19 | 2014 | Lighting Retrofit: LDC classroom T8 group #2 | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -168 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 168 | 84 | 67 | 87 | 4380 | 1750 | 2630 | 36512.28 | 0.07 | 2555.8596 | [15 empty] | 124.5799 | 2555.8596
| CC-20 | 2014 | Lighting Retrofit: LDC globe to LED | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | custom |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 18 | 18 | 62 | 25 | 7300 | 4380 | 2920 | 6175.8 | 0.07 | 432.306 | [15 empty] | 21.0718 | 432.306
| CC-21 | 2014 | Lighting Retrofit: LDC hallway / office T8 group #1 | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -92 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 92 | 92 | 58 | 42 | 5840 | 4380 | 1460 | 14237.92 | 0.07 | 996.6544 | [15 empty] | 48.5798 | 996.6544
| CC-22 | 2014 | Lighting Retrofit: LDC hallway / office T8 group #2 | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -480 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 240 | 240 | 110 | 85 | 5840 | 4380 | 1460 | 64824 | 0.07 | 4537.68 | [15 empty] | 221.1795 | 4537.68
| CC-23 | 2014 | Lighting Retrofit: LDC jelly jar (kitchen coolers / freezers) | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | custom |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 15 | 15 | 23 | 8 | 1460 | 1460 | 0 | 328.5 | 0.07 | 22.995 | [15 empty] | 1.1208 | 22.995
| CC-24 | 2014 | Lighting Retrofit: LDC Photocells (Dining) | capital project |  | Lighting | 5 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -75 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CC-25 | 2014 | Lighting Retrofit: LDC recessed cans to LED | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | custom |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 75 | 75 | 46 | 24 | 7300 | 4380 | 2920 | 17301 | 0.07 | 1211.07 | [15 empty] | 59.031 | 1211.07
| CC-26 | 2014 | Lighting Retrofit: LDC stairwell LED w/ occ. | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -150 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 6 | 6 | 67 | 24 | 8760 | 262.8 | 8497.2 | 3483.6768 | 0.07 | 243.8574
| CC-27 | 2014 | Lighting Retrofit: LDC Wall Mount Occ. Sensor | capital project |  | Lighting | 15 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | -60 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CC-28 | 2014 | Lighting Retrofit: LDC wall wash removal | capital project |  | Lighting | 80 | COMPLETE | 2013-08-05 | LDC | Floors 1-3 |  | Maintenance |  |  | 0 |  | See LDC total | 0 | See LDC total | See LDC total | See LDC total | 77 | 0 | 93 | 0 | 4380 | 0 | 4380 | 31365.18 | 0.07 | 2195.5626 | [15 empty] | 107.018 | 2195.5626
| CC-29 | 2013 | MR16 to LED: LDC | 364555 | WO for in-house labor / parts + TRC: $904.30 Werner invoice S7391408.002: $1446.24 | Lighting | 5 | COMPLETE - did we file for rebate? | 2013-03-29 | LDC | Floors 1-3 |  | Maintenance |  |  |  |  | 0 | 0 | 2350.54 |  | 2350.54 | 113 | 113 | 50 | 10 | 5840 | 5840 | 0 | 26396.8 | 0.07 | 1847.776 | [15 empty] | 90.0659 | 1847.776 | 1.2721
| CC-30 | 2013 | MR16 to LED: Library Rookery | 364711 | TRC invoice ??: $3860 | Lighting | 5 | COMPLETE - rebate received? | 2013-03-22 | Library | Rookery |  | Maintenance |  |  |  |  | 0 | 0 | 3860 | -1048 | 2812 | 28 | 28 | 150 | 16 | 5892 | 5892 | 0 | 22106.784 | 0.07 | 1547.4749 | [15 empty] | 75.4283 | 1547.4749 | 1.8172
| CC-31 | 2013 | Lighting Timers: Musser Corridors |  |  | Lighting | 10 | COMPLETE - fill in details | 2012-11-15 | Musser Hall | Floors 1-4 |  | Students |  |  |  |  | 0 | 100 | 0 | 0 | 100 | [25 empty] | 0 | 0
| CC-32 | 2013 | Lighting Retrofit: Rec Center | capital project |  | Lighting | 15 | COMPLETE - fill in details | 2013-04-01 | Rec Center | Field House |  | Maintenance |  |  |  |  | 36711 | 0 | 0 | -14660 | 22051 | 116 |  | 342 | 168 | 5441 | 5441 |  | 109821.144 | 0.07 | 7687.4801 | [15 empty] | 374.7097 | 7687.4801 | 2.8684
| CC-33 | 2013 | MR16 to LED: Sayles Hill Café |  |  | Lighting | 5 | COMPLETE | 2013-03-29 | Sayle Hill Campus Center | Café Servery |  | Maintenance |  |  |  |  | 0 | 0 |  |  | 0 | [25 empty] | 0 | 0
| CC-34 | 2014 | Lighting Retrofit: High-bay Lighting (3 fixtures) | 376439 | TRC invoice ?? - $830 | Lighting | 15 | COMPLETE - fill in details | 2014-01-21 | Facilities | Garage |  | Maintenance |  | 255 |  |  |  |  | 830 | -255 | 575 |  |  | 885 | 432 | 2500.565 | 2500 | 0 | 1133 | 0.07 | 79.31
| CC-35 | 2014 | Johnson House VFDs (x 4 AHU fans) | 373901 | Mulcahy Invoice 229924 ($1,329) Cedar Lake Invoice 52008 ($2,534.35) | HVAC | 15 | COMPLETE | 2014-01-07 | Johnson House | Mechanical |  | Maintenance | 5882.96 | 3050 | 2832.96 |  | 0 | 0 | 5882.96 | -3050 | 2832.96
| CC-36 | 2015 | Group #2 Elec Meters (17) | Project |  | Meters | 20 | Scheduled for summer 2014 |  | Various | Mech / Elec | [6 empty] | 17000 | 0 | 0 | 0 | not incl.
| CC-37 | 2015 | Group #2 Steam/Cond Meters (13) | Project |  | Meters | 20 | Scheduled for summer 2014 |  | Various | Mech / Elec | [6 empty] | 26000 | 0 | 0 | 0 | not incl.
| CC-38 | 2015 | Watson Stairwell Pilot - ESI fixtures |  |  | Lighting | 15 |  |  | Watson Hall | Stairwells | [6 empty] | 844 | 0 | 0 |  | 844
| CC-39 | 2014 | Gallery Lighting Retrofit | 402224 | TRC invoice ??: $2439 | Lighting | 15 | COMPLETE - rebate received? | 2014-03-05 | Music & Drama | Gallery |  | Maintenance | 4775 | 2336 | 2439 |  |  |  | 4775 |  | 4775 | 68 | 20 | 180.2941 | 43 | 2000 | 2000 | 0 | 22800 | 0.07 | 1596 | [15 empty] | 77.7936 | 1596 | 2.9919
| CC-40 | 2014 | Leighton exit signs to LED | 376254 | Cedar Lake invoice $4500 | Lighting | 15 | COMPLETE - rebate submitted by cedar lake | 2013-12-27 | Leighton Hall | Various |  | Maintenance | 4500 | 575 | 3925 |  | 0 | 0 | 4500 |  | 4500
| CC-41 | 2014 | MH to LED: Leighton Hall (x7 fixtures) | 376310 | Cedar Lake invoice $1480 | Lighting | 15 | COMPLETE - rebate submitted by cedar lake | 2013-12-27 | Leighton Hall |  |  | Maintenance | 1890.19 | 60 | 1830.19 |  | 0 | 0 | 1890.19 |  | 1890.19
| CC-42 | 2014 | Test 4ft LED: Sayles Hill Great Space | 403433 | WO is for test fixture - installed | Lighting | 5 | COMPLETE | 2014-04-03 | Sayle Hill Campus Center | Great Hall |  | Maintenance |  |  |  |  | 0 | 0 | 117 |  | 117 | 1 | 1 | 70.4 | 44.5 | 8760 | 8760 | 0 | 226.884 | 0.07 | 15.8819 | [15 empty] | 0.77413 | 15.8819 | 7.3669
| CC-43 | PENDING | Boliou Artwork lighting |  |  | Lighting | 15 |  |  | Boliou |  |  | Patt Germain
| CC-44 | PENDING | Replace Boliou Fountain Lights |  |  | Lighting | 5 | Summer 2013 fixtures failed; need to redo | 2013-09-06 | Boliou | Exterior |  | Carleton | N/A | N/A | N/A
| CC-45 | PENDING | Solar thermal DHW |  |  | HVAC | 25 |  |  | Cowling | Pool |  | Carleton
| CC-46 | PENDING | Lighting Retrofit: Campus Exterior |  |  | Lighting | 15 |  |  | Exterior | N/A
| CC-47 | 2015 | Steam Plant Lighting Retrofit to LED and induction |  |  | Lighting | 15 | Xcel preapproval received 9/24/14 |  | Facilities | Boiler Room |  | Carleton | 9995 | 709 | 9286 |  |  |  | 9995 |  | 9995 | 13 | 13 | [17 empty] | 0 | 0 | 0 | [6 empty] | Y
| CC-48 | PENDING | Lighting Retrofit: 8ft to 4 ft T8 |  |  | Lighting | 15 |  |  | Stadium | Ground Floor
| CC-49 | PENDING | Lighting Retrofit: HID to T8 |  |  | Lighting | 15 |  |  | Stadium | Hockey Storage Room
| CC-50 | PENDING | Lighting Retrofit: T12 to T8 |  |  | Lighting | 15 |  |  | Stadium | Men's Locker Room T12
| CC-51 | PENDING | Lighting Timers / Occ Sensors : Corridor |  |  | Lighting | 15 |  |  | Stadium | Second Floor
| CC-52 | PENDING | Lighting Timers: Corridor |  |  | Lighting | 15 |  |  | Stadium | Corridors
| CC-53 | PENDING | Group #1 Steam Meter Fixes |  |  | Meters | 20 |  |  | Various | Mech / Elec
| CC-54 | PENDING | Group #2 Gas Meters (4) |  |  | Meters | 20 |  |  | Various | Mech / Elec
| CC-55 | PENDING | Group #2 Water Meters (17) |  |  | Meters | 20 |  |  | Various | Mech / Elec
| CC-56 | PENDING | Hallway lighting timers / occ. |  |  | Lighting | 15 |  |  | Various | Residence Halls
| CC-57 | PENDING | LED Lamps: Exterior Wall Packs |  |  | Lighting | 5 |  |  | Various | Various
| CC-58 | PENDING | Lighting Retrofit: Stairwell Bi-Level LED |  |  | Lighting | 15 |  |  | Various | Stairwells
| CC-59 | PENDING | Occ Sensors: Restrooms |  |  | Lighting | 15 |  |  | Various | Restrooms
| CC-60 | PENDING | Laird Stadium 8 ft T8 retrofit |  |  | Lighting | 15 |  |  | Laird Stadium | Ground Floor
| CC-61 | PENDING | Replace dust extractor with more energy efficient configuration |  |  | HVAC | 20 |  |  | Boliou | Wood shop |  | Stephen Mohring |  | rejected | [36 empty] | The cost of a new recirculating unit that would provide HEPA filtration is significant (50 to 75 grand), I have been seeing units as low as 15k
| CC-62 | PENDING | Replace Chapel exterior architectural lights with LED |  |  | Lighting | 15 |  |  | Chapel | Exterior
| CC-63 | PENDING | Townhouse windows -single pane |  |  | Envelope | 40 |  |  | Townhouses | Exterior
| CC-64 | PENDING | Heat loss that happens in the paint room of the Boliou wood shop, especially when in use. |  |  | Envelope |  |  |  | Boliou | Wood shop |  | Jerry Krause
| CC-65 | PENDING | PRV at the boiler plant to turn down |  |  | Steam Plant |  |  |  | Steam Plant | Boiler Room |  | Mitch Miller
Sayles Hill Rm 253 Lighting Retrofit (4 ft LEDs)
Formulas:
Cost ($) = [Annual Savings]+[Annual Savings ($)]
Annual Savings ($) = [Rate $/kwh]*[kWh Saved]

## Savings Cash Flow
Energy Conservation Measures Tracking Log |  |  | Red Italics = estimate
COMPLETED PROJECTS
GENERAL INFO | [8 empty] | CASH FLOW
Date Recorded | Project | Date Complete | Building | Floor | Room | SF | Auditor | Cost | 2010 |  | 2011 |  | 2012 |  | 2013 |  | 2014 |  | 2015
[9 empty] | kwh | 0.07 | kwh | 0.07 | kwh | 0.07 | kwh | 0.07 | kwh | 0.07 | kwh | 0.07
2013-01-30 | Lighting Retrofit: Library Part 1 | Summer 2010 | Library | 1-4 | All except Reference / Rookery |  | Carleton | #ERROR! | 0 | 0 | 0 | 0 |  | 0 | #ERROR! | #ERROR! |  | 0 |  | 0
2013-01-30 | Lighting Retrofit: Library Part 2 | Summer 2011 | Library | 4 | Reference Room |  | Carleton | #ERROR! | 36512.28 | 2555.8596 | 2555.8596 | 178.9102 |  | 0 | #ERROR! | #ERROR! |  | 0 |  | 0
2013-01-30 | Occupancy Sensors: Stadium | 2012-12-01 | Laird Stadium | 1 | Men's / Women's Locker Rooms |  | DLR Group | #ERROR! | 6175.8 | 432.306 | 432.306 | 30.2614 |  | 0 | #ERROR! | #ERROR! |  | 0 |  | 0
2013-01-30 | Occupancy Sensors: Stadium | 2012-12-01 | Laird Stadium | 1 | Track Area |  | DLR Group | #ERROR! | 64824 | 4537.68 | 4537.68 | 317.6376 |  | 0 | #ERROR! | #ERROR! |  | 0 |  | 0
2013-01-30 | LED Lamps: Exterior Wall Packs | 2012-08-01 | Laird Stadium | 2 | Exterior doors |  | DLR Group | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR!
2013-01-30 | LED Lamps: LDC Part 1 | 2013-01-01 | LDC | 1 | Servery / Dining |  | Carleton | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR!
2012-01-30 | Lighting Retrofit: Grounds Shop | 2012-12-01 | Grounds Shop | 1 | Shop |  |  | #ERROR! | 328.5 | 22.995 | 22.995 | 1.6097 |  | 0 | #ERROR! | #ERROR! |  | 0 |  | 0
2013-01-30 | Lighting Retrofit: West Gym | 2012-08-01 | West Gym | 2 | Main Gym |  |  | #ERROR! | 0 | 0 | 0 | 0 |  | 0 | #ERROR! | #ERROR! |  | 0 |  | 0
2013-01-30 | Lighting Retrofit: Rec Center | 2013-03-01 | Rec Center | 2 | Track and Courts |  | Carleton | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR!
2013-01-30 | Residential Boiler Replacements (12) | Summer 2012 | Various | - | Basement |  |  | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR!
2013-01-30 | DDC Controls / Schedule - AHU 3 | Fall 2012 | Laird Stadium | 3 | Attic |  | DLR Group | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR!
2013-01-30 | LED Lamps |  | Library | 4 | Rookery |  | Carleton | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR! | #ERROR!

## Common ECMs
Common Energy Conservation Measures | Building Assessments | Occupant Survey | Tools of the Trade
Fume hood RxC / Re-balance | General Info | Open Dates | Digital Thermometer
CW Pumping System RxC | Building sf | Open Hours | Sling Psychrometer (seasonal)
HW Pumping System RxC | Building volume | Occupancy | Psychrometric charts
CW / HW temp control valve replacement ( for variable volume pumping) | Building use | Use Patterns - Type | Light Meter
AHU RxC | Annual kW / sf | Custodial | Digital Strobe Tachometer
AHU hot / chilled water coil cleaning | Annual steam / sf | Staff | Ammeter
AHU filter replacement |  | Visitors | Voltmeter
AHU reheat reduction | Loads | Use Patterns - TOD | Wattmeter
Supply / exhaust fan timers | Steam Load | Special Equipment | Air Velocity Meter
Night / weekend setbacks | Cooling Load | Special Air Conditioning | Flue Gas Analyzer (seasonal)
Isolate conditioning for 24/7/365 operation areas | Electrical Load (Peak) | Showers | Dial and Glass Thermometers
Heat wheel/pipe heat recovery | Water Load (Peak) | Steam-fed equipment | Tape measure
Air volume / speed reductions |  |  | Flashlight
Air change rate reductions | Measurements |  | Drill
Reduce exhaust / make-up air CFM | Footcandles |  | Mirror
O.A. "free cooling" opportunities | Amps |  | Screwdriver
Testing & Balancing | Volts |  | Pliers
TOD scheduling: AHUs | Air velocity |  | Ladder
EMS controls upgrade / add'n | Air pressure |  | Hard Hat
Variable Speed Motors: fans | Water velocity |  | Tape
Steam trap replacement / PM | Water pressure |  | Camera
Pipe insulation | Temperature - day/night
Duct insulation |  |  | Estimates
Boiler heat recovery | HVAC components |  | Ventilation | BTU/yr =
Blow-down heat recovery | AHUs |  | Water | BTU/yr =
Drain water heat recovery | Supply Fans |  | Lighting | BTU / yr =
Chiller heat recovery | Return Fans |  | Motors (3 phase) | KWh / yr =
O2 Trim | Exhaust Fans |  | Where:
Chiller plant optimization | HW / CW Pumps |  | TD = Temperature Differential
Temperature parameter adjustments | Coils |  | WD = Watts differenc
EMS upgrades | Ducts |  | cfm = cubic feet per minute
DDC controllers | Dampers |  | HP = horsepower
Replace AHU fan motors w/ VFDs | Diffuser Type |  | gpm = gallons per minute
Localized AC for data / telecom areas | Piping / Insulation |  | k = part load factor
Light fixture replacements (lower wattage, bi-level) | Valves |  | E = efficiency
Light bulb replacements (CFL or LED) | Chillers
Lighting controls - timers | Boilers
Lighting controls - occ. Sensors | Furnaces
Lighting controls - Photo Sensors
Reduced lighting levels | DHW Components
Solid state ballasts | Fuel type
Variable Volume Pumps HW/CW | Tank size
Building shutdown hours | Tank type
Energy efficient AC units
Energy efficient appliances | Lighting Components
Add building sub-meters | Fixture type (s)
Window / door replacement | Ballast type(s)
Door closing operation | Lamp Wattage
Insulation | Controls Timer, Occ, Photo
Roof replacement
Vestibule addition / conditioning | Controls
Weatherstripping / caulking | Thermostats
Tuckpointing | Humidstats
Window shades / coatings | Timers
Summer DHW heaters | Relays
Insulate HW heaters | Actuators
Demand control | Calibration (auto)
High efficiency motors
Improve power factor | Envelope
Exhaust fans tied to lighting | Window Area
Economizer kitchen hood replacement | Door Area
Solar power | Vestibules
Geothermal option | Insulation
Revise building occupancy schedule | Roof type
Pool covers | Heat Loss
Infiltration

## 102 Ideas List
101 Energy Savings Ideas
|  | How they are implemented at Carleton |  | 2002-11-22
Question |  | Currently | Buildings | Suggestion
19 | Watch out for simultaneous heating and cooling! | EMS system controls the building HVAC equipment to prevent this occurrence. The exception is to control the humidity while simultaneously using heat to maintain the machine room temperatures in Mudd. | Mudd | Install a motion sensor or EMS controls in CMC to control fan coil units in classrooms.
20 | Raise the cold air temperature set point at the thermostat. | The Cooling Power and Chiller Operating program (CPOP) is designed to do this based on electric demand. This has not been implemented because a demand limit number has not been provided. | CMC, Hulings, Library, Mudd, Olin & Sayles Hill
21 | Shut down unnecessary auxiliary equipment. | This is controlled by the EMS and implemented throughout campus. Exceptions are: the Chapel air handler, Leighton and Myers exhaust fans which are controlled timers and a smoke fan in Sayles which are controlled by a motion sensor.
22 | Consider using electronic air cleaners in building air handling units in lieu of standard bag or cartridge filters. | No. These are not easy to maintain. Changing prefilters and bag filters are part of the HVAC equipment PM program.
23 | Maintaining cleaner heating and cooling coils by using and regularly changing filters can lead to greater efficiencies. | Yes, this is being performed on mechanical equipment in the Preventative Maintenance (PM) program. The air sides of all coils are cleaned with a pressure washer when needed.
24 | The effectiveness of an energy management system largely depends on the physical condition of the equipment it is intended to control. | The physical condition of the mechanical air handling equipment is addressed by the mechanical PM program. Mechanical HVAC equipment is checked, lubricated, maintained and cleaned regularly and kept in good operating condition. The replacement of 3-way valves with 2-way valves, using VFD's, cog drive belts, and fixed pitch sheaves enhances the mechanical efficiency of the mechanical equipment and systems.
25 | A survey of mechanical systems can reveal a host of opportunities for conserving energy, often at a relatively small initial cost. | The use of ceiling fans in Sayles Hill and in a few offices in Leighton are examples of implementing this opportunity. | Leighton & Sayles Hill
26 | skip | No.
27 | Boiler Controls. | This is opportunity is implemented. Calibration and maintenance of the boiler controls is performed by the Boiler Operators.
28 | Use a boiler blow-down heat exchanger to preheat make-up water going to the deaerator. | This process has been discontinued with the installation of reverse osmosis boiler feed water system. This system minimizes the boiler blow downs required.
29 | Minimize "excess air" in boiler operations. | The system is continuously monitored while the boilers are operating.
30 | For peak efficiency, radiation loss from a boiler should be minimized by keeping insulation in good repair. | Boiler insulation is kept in good repair to save energy.
31 | Insulate exposed hot-water, steam and chilled-water distribution piping where feasible. | Installing pipe insulation on these utilities is performed in new installations. On existing piping, the insulation is checked and repaired on a regular basis. An insulation "repair list" is maintained so identified pipe insulation repairs are addressed.
32 | When specifying piping insulation, look at both the maximum temperature it will be exposed to and the minimum temperature. | This idea is implemented in the facility construction, renovation and maintenance projects.
33 | Whenever medium- or high-pressure steam is used, there will be flash steam from the condensate system. This flash steam contains valuable energy that can be recovered. | This idea is implemented on campus. High pressure steam goes through a flash tank and becomes low pressure steam.
34 | While leakage in the condensate return system is inevitable, such leaks should be kept to a minimum. | Leaks are identified and repaired immediately. The condensate systems in the utility tunnels are continuously being observed. |  | Implement a steam trap PM Program.
35 | Of all the things you can do in a cooling plant to save energy, pumps offer the greatest savings for the least cost. | This is idea is implementation campus. Three-way chilled water valves have been replaced with 2-way valves, requiring less water flow. The chilled water system pressure is kept constant by the variable speed drives on the chilled water pumps.
36 | After reducing system head loss, you will find you have more water running through the system than the chiller and pump can handle within specified limits. | Variable speed drives have been installed on the chilled water system pumps to control the system pressure to a preset set pressure set point. Water flow is reduced when the chilled water system is satisfied.
37 | During renovation or expansion, consider increasing the size of a distribution piping or, in the case of retrofit, adding parallel pipes to double the cross sectional area of the flow path. | Pipe sizing is part of the construction and renovation specifications. This is consideration based on the building load.
38 | Pump and fan capacities can be reduced and energy saved by using variable frequency drives to control their speed. | We agree with this statement. Variable speed drives are used extensively on Campus on HVAC fans and water pumping systems.
39 | Reductions in both peak and off-peak energy costs can be obtained by using variable speed drives on pumps, fans and compressors that operate at varying loads. | A number of locations have Variable Frequency Drives on hot water systems: The following locations do not Variable Frequency Drives on hot water systems: Boliou, Davis, Goodhue,Leighton, Library, M&D, Mudd, Musser, Myers, Olin, and Sayles Hill. | Burton, CMC, Hulings, LDC, Nourse, Rec Center, Student Housing and Watson, | The following locations: Musser, Myers & Watson should have the heating systems redone. These systems are not controlled with VFD's. The heating valves for Watson ready to install. Locations that should be updated: Boliou, Davis, Goodsell, Leighton, Library, M&D, Mudd, Musser, Myers, Olin and Sayles Hill.
40 | Changing from a terminal reheat system, which provides good thermal comfort but is known for its poor energy efficiency, to a variable air volume system can have significant savings. | ????
41 | Many variable air volume fans operate at constant speed over the system's entire operating flow range. | There are inlet control veins are on the Sayles Hill, Library and Laird HVAC systems. VFD's are better and perform more efficiently. |  | Install VFD's on Laird, Library (2) and Laird all handling units and disconnect the inlet control veins.
42 | Think system efficiency when making decisions about conservation strategies. | A chiller optimization program (CPOP) has been installed and controls the cooling tower operation. This system optimizes the cooling tower operation by varying cooling tower motor speed and multiple towers operation. (For example, two cooling tower motors are run at 50% instead of one at 100%.) Variable frequency drives have been installed on the chilled water primary pumps. These VFD's vary the pump speeds with the Campus chilled water load. Campus chilled water secondary pumps, while in place, are not turned on. | Facilities
43 | The coefficient of performance can be improved by raising the chilled water supply temperature and lowering the condenser water temperature. | We lower condenser water temperature when feasible but do not raise chilled water temperature. CMC and other areas require a constant chilled water temperature for their operations.
44 | Monitor outside air temperature and humidity to control chilled water supply temperature (chilled water reset strategy). | This process is not followed. The chilled water temperature needs to be constant to take care of CMC computer room needs. |  | Institute chilled water reset strategy after the new CMC cooling system is installed. Consider this strategy when designing the new CMC computer room cooling system.
45 | Consider installing instrumentation to monitor real-time, cooling plant efficiency in kw/ton. | A chiller optimization program (CPOP) operates the most efficient chiller to perform this function.
46 | Cooling towers are one of the most overlooked opportunities for saving energy in cooling plants. | The cooling tower fans are controlled with variable frequency drives. These fans are programmed so the most efficient tower operation is maintained.
47 | To improve cooling tower efficiency, lower the cooling tower fan horsepower by adding surface area and free area within a tower fill. | This is being done in the chiller plant. Water is run through all the cooling towers to utilize free cooling, even with some of the cooling tower fans are off.
48 | In multiple tower/chiller installations, run all the water over all the fill when possible. | Agree with this statement. This is addressed in item 47.
49 | Consider controlling all the cooling tower fans with one variable frequency drive and modulate the fan speed together. | The cooling tower motors are on Variable Frequency Drives that are controlled with the CPOP. This program optimizes efficiency of the cooling tower operation.
50 | Control cooling tower fans by sensing ambient wet bulb (wb) temperature. | The wet bulb temperature is considered when operating the cooling tower water temperatures above 65 degrees. The CPOP program controls the cooling tower fan speeds through the VFD's to optimize cooling tower efficiency. Below 65 degrees, cooling tower temperatures are controlled by the VFD's operation only.
51 | Reuse waste heat. | These buildings use heat recovery systems, where the exhaust heat is recovered to preheat the supply air for the air handlers. The Hulings and Mudd heat recovery systems are part of the building systems. Only the Locker Room heat is recovered in the Rec Center. | Hulings, Mudd and Rec. Center
52 | The installation of an economizer, a device that preheats the feed water (returned condensate), typically will increase the efficiency of a boiler by 2 to 3 percent. | Boiler #3 has an economizer installed. | Facilities
53 | Provide all air handling units with an economizer with enthalpy control. | The facilities EMS uses this technology system controls the building HVAC systems.
54 | Investigate using the economizer cycle to sub cool a building at night. | This process is utilized in the Rec Center in the summer. In the winter, the dry coolers on the roof of the Facilities building are used to cool the chilled water system. This system cools CMC, the Library Archives and science projects in the science buildings. | CMC, Hulings, Library, Mudd and Olin
55 | Consider free cooling with cooling towers in commercial buildings and industrial plants where space conditioning or process cooling is done with mechanical refrigeration. | The dry coolers on the Facilities Building are used in the winter to cool the Campus chilled water loop. A steam operated still was installed in the Boiler room to remove oil from the Campus air compressor blow downs. (The steam system is more efficient than the electric system it replaced.) | Facilities
56 | Using a water-side economizer system instead of the more common air-side economizer when the air supplied to the space must be kept within close humidity limits. | The existing cooling towers are not designed for winter operation and there is a fear of freezing the HVAC coils. |  | Install VFD's on Laird, Library (7) and Laird all handling units and disconnect the inlet control veins.
57 | More may be better than less when it comes to saving energy. | This process is used in most off campus houses where two heating boilers are installed. The boilers are installed in tandem, where one boiler runs the system until it cannot handle the load, then the second one operates to take up the remaining load. Tandem hot water heater are utilized in Parish and Huntington houses employing this same principle.. | Off campus houses. Huntington & Parish Houses
58 | Often, critical items of equipment are provided with 100 percent redundancy. (One standby operates when the normal unit is out-of-service.) | Heating pumps are 100% redundant. Their operation is switched every 15 days by the EMS system. This provides heating system reliability.
59 | Consider installing water-loop heat pumps. | This would not be effective on campus. It would require more pipes to be buried and zigzag between existing water lines.
60 | Consider a thermal storage system when designing your chiller plant. With a thermal storage system, the idea is to run chiller equipment off-peak and store cooled water or ice, then draw on this cooling during the day. | This has idea was considered in the past. The ice storage would have to be close to the facilities building to be effective. The excavation cost in the limestone around the Facilities Building was deemed too expensive to make this idea feasible.
61 | Steam turbines can be used to recover valuable energy from pressure reducing valves (PRVs). | The campus steam pressure is not sufficient to support a steam turbine.
62 | For some areas of the country, evaporative rooftop cooling is reducing summer cooling loads by as much as 25 percent. | The facility cooling towers use the evaporative cooling principle. The CPOP program controlling Variable Frequency Drives fan motors are used optimize cooling tower operations. There are three campus evaporative coolers. One on each of the Campus green houses. | Campus Green Houses
63 | Although a domestic hot-water system accounts for only about 4 percent of a building's total energy consumption (that figure is higher in buildings having a laundry or restaurant), increasing the system's energy efficiency is nonetheless worthwhile. | The Severance domestic hot water system was removed from the Facilities building tank. The new system was installed in the building during the recent renovation. The systems temperature is controlled by the EMS. The new Sevy domestic hot water system was designed to high efficiency operating standards using new equipment and adequate systems insulation. | Severance
64 | Reduce generating and storage temperature levels to the minimum required for washing hands - usually 105 F. | Domestic hot water temperatures are set to 120 degrees. This allows for distribution heat loss in most buildings. Producing domestic water at 105 degrees does not provide adequate hot water for showers. In the Rec Center, the domestic water for the showers is generated at 110 degrees, for slop and hand sinks at 120 degrees and for the washers at 140 degrees. | Rec Center
65 | If there is a need for process heat within an operation, a heat reclaimer can be installed in the boiler stack instead of an economizer. | The steam load is not big enough to support this year round.
66 | If water pressure exceeds 40 to 50 pounds, consider having a plumber install a pressure-reducing valve on the main service to restrict the amount of hot water that flows from a tap. | Reducing water pressure is not done. Campus showers are equipped with water saver heads and aerators are installed on sink faucets to reduce water usage.
67 | When considering lighting systems retrofits, remember that the least expensive part of the system on a life-cycle basis is the fixture and lamp. | Light fixtures are specified by the AE firms for construction and renovating projects. The recent projects have dictated the type of lighting utilized. The college standard is good fixtures with long life, energy efficient fluorescent lamps. |  | Give college final approval of fixtures and lamps during the construction and renovation design process.
68 | There are three ways in which lighting energy use can be reduced by building owners: implement a greater degree of control over the use of lighting, use more efficient lighting equipment and apply better lighting system design strategies. | A sophisticate light controlling system has been installed in LDC. This system controls classroom light levels. It also controls light on-off operation in the eating areas. The corridors and common area light are controlled by motion sensors. The light levels in Great Hall are controlled outside light sensors. | LDC & Severance
69 | When incorporating energy-efficient lighting technologies, it's important to remember that every facility is different. | Incorporating energy-efficient lighting through out Campus is considered. It depends on the usage. Circle line fluorescent (54 Watts) and incandescent fixtures (100 Watts) have been replaced by Broadwax fixtures (41 Watts) using efficient compact florescent lamps. Metal halide and high pressure sodium lighting is also utilized in many applications. Outside light fixture have been changed to provide a broader light diffusion pattern, therefore using less fixtures.
70 | When retrofitting an existing lighting system, look at the task being performed in the space. | Retrofitting of light fixtures have been performed on a case -by-case basis. 100 Watt incandescent and 54 watt circle line fixtures have been replaced with 41 watt Broadwax fixtures, that use 3 -13 watt compact florescent lamps. This has been done during the "Spruce Up" of college houses and various Campus building renovations. | Renovation and "Spruce up" Projects
71 | Don't let first cost deter you from investigating some of the more energy-efficient lighting technologies. | The pattern has been not to let this dictate lower level. The use of Broadwax and the fluorescent fixtures with T8 lamps has been the campus standard since the early 90's. Using the same style standardized fixtures provides for easier light fixture maintenance and fewer parts requirements.
72 | Lighting control is perhaps the most important element of any lighting energy conservation program. | There are occupancy and ambient light sensors in LDC. Great Hall has an ambient light sensor. | LDC & Severance | The lighting scenes and number of these scenes plus the location for the auxiliary control location needs to be determined.
73 | Incorporate motion detectors where they make sense. | Motion sensors are being utilized in the offices and hallways of LDC. The motion sensors in the LDC restrooms however they have been bypassed since they do not meet the users needs. | LDC | Other areas a motion/occupancy sensor would be effective would be in Academic Classrooms, Boliou, Hulings, Mudd, and Olin.
74 | Full-range and "step" fluorescent dimming systems can significantly reduce the power delivered to fluorescent lights and can even be activated in response to available daylight for perimeter areas. | Areas with these dimming systems are: LDC classrooms, Sayles Hill 251, 252, 253, 254 & Hill lounge, Boliou Auditorium & Great Hall. | Boliou, LDC, Sayles Hill & Severance
75 | The T8 system is, in most cases, the best retrofit method for existing fluorescent lamps. | Since the early 90's the T8 energy efficient lamps using electronic ballasts have been standard on campus. They have replaced the T12 lamps and low efficiency wire wound ballasts. The T8 system is not used in the Library six foot fixtures and the Book Security system. The T8 lamps interfere with the Security system.
76 | Fixtures that have state-of-the-art lamps or ballast's (T8 lamps, electronic ballast's, etc.) may save plenty of energy but may also require a higher premium at relamping or reballasting time. | The standard is to use fixtures with longer life fluorescent bulbs and high efficiency solid state lighting ballasts. The standard lamp is a Philips Alto which has 24,000 hr life. |  | Areas to replace T12 with T8's are: Chapel, Music and Drama, Sayles Hill (corridor and storage), Stadium (Student rooms) Willis
77 | Even if you have already retrofitted a lighting system with energy-efficient core-coil ballast's and "watt miser" lamps, you can get further savings with a T8 conversion. | Since the early 90's the use of the T12 fluorescent lamps with low efficiency ballasts was discontinued. They have systematically been replaced with T8 fluorescent lamps and high efficiency electronic ballasts.
78 | It's a good idea to replace incandescent lamps with compact fluorescents (CFLs). | The College standard is to replace incandescent (100 watt) fixtures with Broadwax (41 watt) compact fluorescent and/or LB2/32 florescent (66 watt) fixtures. Exception is Sayles Lounge classrooms where incandescent lamps still exist since light dimming is required.
79 | Replace your 10-,15- or 20-watt incandescent lamps in exit signs with 5- or 7-watt compact fluorescents (CFLs). | The College standard is to use Exitonics solid state LED type exit lights. Any existing incandescent lamps are 7.5 watt. (2 lamps each) |  | Replace existing fluorescent exit lamps with Exitronics LED type when they burn out.
80 | Get rid of all mercury lamps inside or outside the building! | All campus mercury lamps have been replaced with metal halide. Notable places where they existed were: Library, Mudd and Olin
81 | What does all the hype mean? | Baldor Super E motors are the Campus standard. Carleton started using them in conjunction with NSP rebate incentives. These motors have proved to be efficient, reliable and have a long life span.
82 | How long should a motor last? | Too many variables to incorporate into a blanket statement.
83 | The nameplate is a motor's single most important component. NEMA standards require certain information on all AC motor nameplates. The major items any nameplate must display are: | The motor name plate data is being captured and incorporated into the Facility Wizard PM program.
84 | When the subject of efficiency comes up, motor users usually get this advise: "Get rid of those oversized motors. Replace them with motors rated closer to the actual load horsepower, and you'll save energy." | This is determined case by the case. This has been achieved using High E Baldor, high efficiency motors that are controlled with Variable Frequency Drives.
85 | Do the savings from the lower motor losses of an energy-efficient motor justify the extra motor cost? | Agree with the statement. Baldor, High E, high efficiency motors have proved to be more efficient, reliable and have a longer life span.
86 | Will "soft starting" save money? | Currently, Soft Start is used on large ticket motors only. | Campus Well
87 | Do "power factor controllers" save energy? | Power Factor Correction is the standard for the campus electrical service. There are capacitor banks located on the Facilities midlevel and at Leighton. | Facilities & Leighton
88 | Need some troubleshooting tips? | This will be more effectively tracked with the Facility Wizard PM program.
89 | Perform an elevator traffic review to determine if a building is properly service based on time-of-day use. | Not controlled by Facilities.
90 | If escalators are installed, consider these alternatives: | Greg
91 | Do not permit elevators to time out and shut down too rapidly. | Greg
92 | Can you cost-justify retrofitting older elevators? | Predominately the elevators are hydraulic and a few cable operated. The elevators are being changed based on cost and safety requirements.
93 | Encourage employees to turn off computers and displays, printers, and copiers when they are not being used (nights, weekends, lunch periods, etc.) | ITS & Res Life Initiatives
94 | Don't forget about printers and copiers. | Incorporated into new printers and copiers.
95 | Portable may be better when it comes to computers. | ITS
96 | Consider purchasing advanced ink jet or impact (dot matrix) printers for work stations while sharing large or high-quality printers among several people. | ITS
97 | Don't lose interest in a project. | AND?
98 | To avoid losing efficiency, calibrate pneumatic thermostats every three to six months, depending on the condition of the control air supply and the frequency of tampering by occupants. | Most pneumatic thermostats have been removed and replaced using dampers/valves on Air Handling Units controlled by EMS.
99 | Make sure it's plugged in! | This will be more effectively tracked with the PM program.
100 | Energy efficiency improvements also boost employee productivity. | Campus temperature situations, too hot or cold, are addressed immediately.
101 | Look for opportunities. | This occurs during redesign/renovations.
102 | Having read through 101 Energy Saving Ideas, undoubtedly you have a hot tip or two of your own. If you'd like to submit an idea ---- | Read and discussed 101 energy saving ideas. |  | -Replace Pressure dependent boxes in Leighton with Pressure independent boxes. -On multi- zone systems monitor zone dampers and reset hot and cold decks based On the warmest and coldest zones.
Wayne Beierman
Kerry Dwyer
Don Smith

## Library Verify
Library Lighting Retrofit: Electricity Savings Verification
Phase 1: Fixture replacements complete
Phase 2: Controls upgrade in place
Phase 3: Reference Room retrofit complete
Historical Usage (kWh)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
2006 |  |  |  |  | 115859 | 114077 | 65030 | 87150 | 72036.2 | 123029.8 | 92658 | 76280
2007 | 85909 | 89067 | 107482 | 93550 | 101348 | 89780 | 52405.7 | 80693.5 | 65460 | 97513.1 | 55758.1 | 64255.6
2008 | 86005 | 64784 | 62464 | 97614.2 | 60578.2 | 72728 | 48910.6 | 62360 | 59850 | 80660 | 65250 | 57920
2009 | 76279.4 | 83665.6 | 65454.6 | 90672.2 | 93062.4 | 79810.8 | 62482.4 | 57255.6 | 89137 | 74244 | 73226.4 | 57669.6
2010 | 57313.6 | 79686.4 | 40000 | 75000 | 63350.8 | 49162.4 | 49286.8 | 39200 | 39000 | 56500 | 38100 | 34300
2011 | 51800 | 42200 | 47700 | 44200
2012
2013
2014
| 34614 | 31920 | 41177 | 49472 | 42997 | 38213 | 57153 | 57681 | 58284 | 60015 | 64933 | 49438
Monthly Averages Comparisons (kWh)
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Historical Avg | 76376.75 | 79300.75 | 68850.15 | 89209.1 | 86839.68 | 81111.64 | 57207.175 | 71864.775 | 71620.8 | 93861.725 | 71723.125 | 64031.3
Actual Usage 2010 | Monthly Averages Comparisons (kWh) Jul: 49286.8; Monthly Averages Comparisons (kWh) Aug: 39200; Monthly Averages Comparisons (kWh) Sep: 39000; Monthly Averages Comparisons (kWh) Oct: 56500; Monthly Averages Comparisons (kWh) Nov: 38100; Monthly Averages Comparisons (kWh) Dec: 34300
Actual Usage 2011 | Monthly Averages Comparisons (kWh) Jan: 51800; Monthly Averages Comparisons (kWh) Feb: 42200; Monthly Averages Comparisons (kWh) Mar: 47700; Monthly Averages Comparisons (kWh) Apr: 44200
Reduction: Actual - Avg usage | 24576.75 | 37100.75 | 21150.15 | 45009.1 |  |  | 7920.375 | 32664.775 | 32620.8 | 37361.725 | 33623.125 | 29731.3
Savings at 0.06/kWh | 1474.605 | 2226.045 | 1269.009 | 2700.546 |  |  | 475.2225 | 1959.8865 | 1957.248 | 2241.7035 | 2017.3875 | 1783.878
Yearly Savings
Avg yearly usage 06-10 (kWh) | Monthly Averages Comparisons (kWh) Jan: 911997
FY 2010 usage (kWh) | Monthly Averages Comparisons (kWh) Jan: 530745; Monthly Averages Comparisons (kWh) Feb: (Averages used for May and June until data are available)
Usage reduction (kWh) | Monthly Averages Comparisons (kWh) Jan: 381252
Yearly Savings at 0.06/kWh | Monthly Averages Comparisons (kWh) Jan: 22875